## Cable
Name | Shortname | Info | Unom | Price | R | X | C | Tan_delta | R0 | X0 | C0 | Inom0 | G1 | Inom1 | G2 | Inom2 | G3 | Inom3 | Ik1s | TR | TInom | TIk1s | Frequency | VoP
|  |  | kV | /m | Ohm/km | Ohm/km | µF/km |  | Ohm/km | Ohm/km | µF/km | A | Km/W | A | Km/W | A | Km/W | A | kA | °C | °C | °C | Hz | m/µs
3x95Cu GPLK | 95 Cu |  | 10 | 0 | 0.216 | 0.083 | 0.33 | 0.003 | 1.826 | 0.75 | 0.165 | 160 | 0.5 | 245 | 0.75 | 225 | 1 | 210 | 12.255 | 50 | 50 | 160 | 50 | 168
3x240Al XLPE | 240 Al X |  | 10 | 0 | 0.162 | 0.089 | 0.45 | 0.0004 | 0.68 | 0.339 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 150
12/20kV 3x240Alrm+as50 P1MeKrv-as lqwd | 240 Al X |  | 20 | 0 | 0.162 | 0.098 | 0.3 | 0.0004 | 0.68 | 0.339 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 168
12/20kV 1x240Alrm+as25 YMeKrv-as lqwd | 240 Al Xd |  | 20 | 0 | 0.161 | 0.124 | 0.29 | 0.0004 | 0.814 | 0.1 | 0.29 | 495 | 0.5 | 394 | 0.75 | 355 | 1 | 333 | 22.8 | 90 | 90 | 250 | 50 | 168
3x240Al GPLK | 240 Al |  | 10 | 0 | 0.139 | 0.075 | 0.47 | 0.003 | 1.18 | 0.631 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 50 | 50 | 160 | 50 | 168
3x150Al XLPE | 150 Al X |  | 10 | 0 | 0.265 | 0.093 | 0.37 | 0.0004 | 0.928 | 0.1 | 0.37 | 330 | 0.5 | 310 | 0.75 | 280 | 1 | 266 | 14.25 | 90 | 90 | 250 | 50 | 150
3x95Al XLPE | 95 Al X |  | 10 | 0 | 0.411 | 0.102 | 0.32 | 0.0004 | 1.089 | 0.1 | 0.32 | 250 | 0.5 | 238 | 0.75 | 215 | 1 | 204 | 9.025 | 90 | 90 | 250 | 50 | 150
12/20kV 1x240Alrm+as35 YMeKrv-as lqwd | 240 Al Xd |  | 20 | 0 | 0.161 | 0.118 | 0.29 | 0.0004 | 0.814 | 0.1 | 0.29 | 580 | 0.5 | 405 | 0.75 | 365 | 1 | 343 | 22.8 | 90 | 90 | 250 | 50 | 168
6/10kV 3x240Alrm+as70 YMeKrv-as lqwd | 240 Al X |  | 10 | 0 | 0.162 | 0.089 | 0.45 | 0.0004 | 0.68 | 0.339 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 150
12/20kV 3x240Alrm+as50 YMeKrv-as lqwd | 240 Al X |  | 20 | 0 | 0.162 | 0.098 | 0.3 | 0.0004 | 0.68 | 0.339 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 168
3x35Cu GPLK | 35 Cu |  | 10 | 0 | 0.586 | 0.093 | 0.26 | 0.003 | 1.35 | 1.68 | 0.13 | 89 | 0.5 | 145 | 0.75 | 135 | 1 | 125 | 4.515 | 50 | 50 | 160 | 50 | 168
3x150Al GPLK | 150 Al |  | 10 | 0 | 0.229 | 0.079 | 0.39 | 0.003 | 1.537 | 0.682 | 0.195 | 165 | 0.5 | 250 | 0.75 | 230 | 1 | 215 | 12.75 | 50 | 50 | 160 | 50 | 168
3x50Al GPLK | 50 Al |  | 10 | 0 | 0.713 | 0.089 | 0.28 | 0.003 | 1.48 | 1.57 | 0.14 | 83 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 4.25 | 45 | 50 | 160 | 50 | 168
3x95Al GPLK | 95 Al |  | 10 | 0 | 0.356 | 0.082 | 0.34 | 0.003 | 1.24 | 1.38 | 0.17 | 125 | 0.5 | 205 | 0.75 | 185 | 1 | 170 | 8.075 | 50 | 50 | 160 | 50 | 168
3x70Cu GPLK | 70 Cu |  | 10 | 0 | 0.3 | 0.085 | 0.31 | 0.003 | 1.16 | 1.44 | 0.155 | 135 | 0.5 | 215 | 0.75 | 195 | 1 | 180 | 9.03 | 50 | 50 | 160 | 50 | 168
6/10kV 3x95Alrm+as50 YMeKrv-as lqwd | 95 Al X |  | 10 | 0 | 0.411 | 0.102 | 0.32 | 0.0004 | 1.089 | 0.1 | 0.32 | 250 | 0.5 | 238 | 0.75 | 215 | 1 | 204 | 9.025 | 90 | 90 | 250 | 50 | 150
3x16Cu GPLK | 16 Cu |  | 10 | 0 | 1.218 | 0.113 | 0.17 | 0.003 | 3.224 | 1.242 | 0.085 | 55 | 0.5 | 80 | 0.75 | 80 | 1 | 80 | 2.064 | 35 | 50 | 160 | 50 | 168
3x150Cu GPLK | 150 Cu |  | 10 | 0 | 0.139 | 0.079 | 0.39 | 0.003 | 1.06 | 1.15 | 0.195 | 210 | 0.5 | 320 | 0.75 | 295 | 1 | 275 | 19.35 | 50 | 50 | 160 | 50 | 168
8/10kV 3x25Cu GPLK | 25 Cu |  | 10 | 0 | 0.813 | 0.097 | 0.23 | 0.003 | 1.55 | 1.73 | 0.115 | 74 | 0.5 | 120 | 0.75 | 110 | 1 | 105 | 3.225 | 50 | 50 | 160 | 50 | 168
3x35Cu VG-GPLK | 35 Cu |  | 10 | 0 | 0.586 | 0.093 | 0.26 | 0.003 | 1.35 | 1.68 | 0.13 | 89 | 0.5 | 145 | 0.75 | 135 | 1 | 125 | 4.515 | 50 | 50 | 160 | 50 | 168
3x185Al GPLK | 185 Al |  | 10 | 0 | 0.182 | 0.077 | 0.42 | 0.003 | 1.46 | 0.66 | 0.21 | 190 | 0.5 | 290 | 0.75 | 265 | 1 | 245 | 15.725 | 50 | 50 | 160 | 50 | 168
12/20kV 3x240Alrm+as70 YMeKrv-as lqwd | 240 Al X |  | 20 | 0 | 0.162 | 0.098 | 0.3 | 0.0004 | 0.68 | 0.339 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 168
20kV-3x240Al XLPE | 240 Al X |  | 20 | 0 | 0.162 | 0.089 | 0.3 | 0.0004 | 0.68 | 0.339 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 150
3x240Al VG-GPLK | 240 Al |  | 10 | 0 | 0.139 | 0.075 | 0.47 | 0.003 | 1.18 | 0.631 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 50 | 50 | 160 | 50 | 168
3x240Cu GPLK | 240 Cu |  | 10 | 0 | 0.084 | 0.075 | 0.47 | 0.003 | 1.06 | 1.15 | 0.235 | 285 | 0.5 | 430 | 0.75 | 390 | 1 | 365 | 30.96 | 50 | 50 | 160 | 50 | 168
_3x240Al GPLK | 240 Al |  | 10 | 0 | 0.14037 | 0.074577 | 0.47 | 0.003 | 1.1459 | 0.83097 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 20 | 50 | 160 | 50 | 168
_12/20kV 3x240Alrm+as50 YMeKrv-as lqwd | 240 Al X |  | 20 | 0 | 0.1636 | 0.097447 | 0.3 | 0.0004 | 0.66038 | 0.44643 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 20 | 90 | 250 | 50 | 168
_12/20kV 1x630Alrm+as50 YMeKrv-as lqwd | 630 Al Xd |  | 20 | 0 | 0.063621 | 0.099436 | 0.46 | 0.0004 | 0.68562 | 0.13169 | 0.43 | 910 | 0.5 | 655 | 0.75 | 575 | 1 | 554 | 59.85 | 20 | 90 | 250 | 50 | 168
_3x240Al XLPE | 240 Al X |  | 10 | 0 | 0.1636 | 0.088498 | 0.45 | 0.0004 | 0.66038 | 0.44643 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 20 | 90 | 250 | 50 | 150
_3x240Al GPLK | 240 Al |  | 10 | 0 | 0.14194 | 0.075527 | 0.47 | 0.003 | 1.1554 | 0.82605 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 20 | 50 | 160 | 50 | 168
_12/20kV 3x240Alrm+as50 YMeKrv-as lqwd | 240 Al X |  | 20 | 0 | 0.16543 | 0.098689 | 0.3 | 0.0004 | 0.6658 | 0.44379 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 20 | 90 | 250 | 50 | 168
_12/20kV 1x630Alrm+as50 YMeKrv-as lqwd | 630 Al Xd |  | 20 | 0 | 0.064334 | 0.1007 | 0.46 | 0.0004 | 0.69125 | 0.13091 | 0.43 | 910 | 0.5 | 655 | 0.75 | 575 | 1 | 554 | 59.85 | 20 | 90 | 250 | 50 | 168
_3x150Cu GPLK | 150 Cu |  | 10 | 0 | 0.12495 | 0.085262 | 0.39 | 0.003 | 0.96986 | 1.2503 | 0.195 | 210 | 0.5 | 320 | 0.75 | 295 | 1 | 275 | 19.35 | 20 | 50 | 160 | 50 | 168
_3x240Al GPLK | 240 Al |  | 10 | 0 | 0.12495 | 0.080945 | 0.47 | 0.003 | 1.0797 | 0.68602 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 20 | 50 | 160 | 50 | 168
_12/20kV 3x240Alrm+as50 YMeKrv-as lqwd | 240 Al X |  | 20 | 0 | 0.14563 | 0.10577 | 0.3 | 0.0004 | 0.62217 | 0.36856 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 20 | 90 | 250 | 50 | 168
1x630Al XLPE | 630 Al Xd |  | 10 | 0 | 0.063 | 0.103 | 0.4 | 0.0004 | 0.275 | 0.101 | 0.66 | 910 | 0.5 | 655 | 0.75 | 575 | 1 | 554 | 59.85 | 90 | 90 | 250 | 50 | 168
_3x150Cu GPLK | 150 Cu |  | 10 | 0 | 0.12316 | 0.083255 | 0.39 | 0.003 | 0.85013 | 1.4706 | 0.195 | 210 | 0.5 | 320 | 0.75 | 295 | 1 | 275 | 19.35 | 20 | 50 | 160 | 50 | 168
_3x95Cu GPLK | 95 Cu |  | 10 | 0 | 0.19139 | 0.087471 | 0.33 | 0.003 | 1.4645 | 0.95911 | 0.165 | 160 | 0.5 | 245 | 0.75 | 225 | 1 | 210 | 12.255 | 20 | 50 | 160 | 50 | 168
_3x150Al XLPE | 150 Al X |  | 10 | 0 | 0.23481 | 0.098009 | 0.37 | 0.0004 | 0.74427 | 0.12788 | 0.37 | 330 | 0.5 | 310 | 0.75 | 280 | 1 | 266 | 14.25 | 20 | 90 | 250 | 50 | 150
_3x240Al GPLK | 240 Al |  | 10 | 0 | 0.12316 | 0.07904 | 0.47 | 0.003 | 0.94638 | 0.80693 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 20 | 50 | 160 | 50 | 168
12/20kV 1x630Alrm+as50 YMeKrv-as lqwd | 630 Al Xd |  | 20 | 0 | 0.063 | 0.1 | 0.46 | 0.0004 | 0.706 | 0.1 | 0.43 | 910 | 0.5 | 655 | 0.75 | 575 | 1 | 554 | 59.85 | 90 | 90 | 250 | 50 | 168
_3x150Cu GPLK | 150 Cu |  | 10 | 0 | 0.12649 | 0.082043 | 0.39 | 0.003 | 1.0059 | 1.1772 | 0.195 | 210 | 0.5 | 320 | 0.75 | 295 | 1 | 275 | 19.35 | 20 | 50 | 160 | 50 | 168
_3x240Al GPLK | 240 Al |  | 10 | 0 | 0.12649 | 0.077889 | 0.47 | 0.003 | 1.1197 | 0.64591 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 20 | 50 | 160 | 50 | 168
_3x240Al XLPE | 240 Al X |  | 10 | 0 | 0.14743 | 0.092428 | 0.45 | 0.0004 | 0.64527 | 0.34701 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 20 | 90 | 250 | 50 | 150
_3x150Cu GPLK | 150 Cu |  | 10 | 0 | 0.13095 | 0.086326 | 0.39 | 0.003 | 0.98527 | 1.1746 | 0.195 | 210 | 0.5 | 320 | 0.75 | 295 | 1 | 275 | 19.35 | 20 | 50 | 160 | 50 | 168
_3x240Al GPLK | 240 Al |  | 10 | 0 | 0.13095 | 0.081955 | 0.47 | 0.003 | 1.0968 | 0.64447 | 0.235 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 290 | 20.4 | 20 | 50 | 160 | 50 | 168
_3x240Al XLPE | 240 Al X |  | 10 | 0 | 0.15262 | 0.097253 | 0.45 | 0.0004 | 0.63206 | 0.34624 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 20 | 90 | 250 | 50 | 150
6/10kV 3x95Alrm+as70 YMeKrv-as lqwd | 95 Al X |  | 10 | 0 | 0.411 | 0.102 | 0.32 | 0.0004 | 1.089 | 0.1 | 0.32 | 250 | 0.5 | 238 | 0.75 | 215 | 1 | 204 | 9.025 | 90 | 90 | 250 | 50 | 150
Alliander 20kV 3x240Al | 240 Al X |  | 20 | 0 | 0.162 | 0.098 | 0.3 | 0.0004 | 0.68 | 0.339 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 168
3x35Cu GPLK 10.5 | 35 Cu |  | 10 | 0 | 0.586 | 0.093 | 0.26 | 0.003 | 1.35 | 1.68 | 0.13 | 89 | 0.5 | 145 | 0.75 | 135 | 1 | 125 | 4.515 | 50 | 50 | 160 | 50 | 168
12/20kV 3x240Al YMeKrv-as lwd | 240 Al X |  | 20 | 0 | 0.162 | 0.098 | 0.3 | 0.0004 | 0.68 | 0.339 | 0.3 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 168
6/10kV 3x240Al+as70 YMeKrv-as qwd | 240 Al X |  | 10 | 0 | 0.162 | 0.089 | 0.45 | 0.0004 | 0.68 | 0.339 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 150
3x35Al GPLK | 35 Al |  | 10 | 0 | 0.965 | 0.093 | 0.26 | 0.003 | 1.72 | 1.67 | 0.13 | 69 | 0.5 | 110 | 0.75 | 105 | 1 | 97 | 2.975 | 50 | 50 | 160 | 50 | 168
3x50Cu GPLK | 50 Cu |  | 10 | 0 | 0.432 | 0.09 | 0.27 | 0.003 | 1.24 | 1.55 | 0.135 | 105 | 0.5 | 160 | 0.75 | 150 | 1 | 140 | 6.45 | 50 | 50 | 160 | 50 | 168
6/10kV 3x95Alrm+as50 P1MeKrv-as lqwd | 95 Al X |  | 10 | 0 | 0.411 | 0.102 | 0.32 | 0.0004 | 1.089 | 0.1 | 0.32 | 250 | 0.5 | 238 | 0.75 | 215 | 1 | 204 | 9.025 | 90 | 90 | 250 | 50 | 150
3x95Cu XLPE | 95 Cu X |  | 10 | 0 | 0.247 | 0.105 | 0.31 | 0.0004 | 0.909 | 0.1 | 0.31 | 315 | 0.5 | 375 | 0.75 | 335 | 1 | 310 | 13.585 | 90 | 90 | 250 | 50 | 168
3x50Al XLPE | 50 Al X |  | 10 | 0 | 0.822 | 0.089 | 0.24 | 0.0004 | 1.541 | 0.1 | 0.24 | 220 | 0.5 | 177 | 0.75 | 160 | 1 | 150 | 4.75 | 90 | 90 | 250 | 50 | 168
12/20kV 1x25Cu+as16 YMeKrv-as lqwd | 25 Cu X- |  | 20 | 0 | 0.927 | 0.248 | 0.15 | 0.0004 | 1.861 | 0.1 | 0.15 | 180 | 0.5 | 150 | 0.75 | 135 | 1 | 127 | 3.325 | 90 | 90 | 250 | 50 | 168
6/10kV 3x240Alrm+as50 YMeKrv-as lqwd | 240 Al X |  | 10 | 0 | 0.162 | 0.089 | 0.45 | 0.0004 | 0.68 | 0.339 | 0.45 | 455 | 0.5 | 399 | 0.75 | 360 | 1 | 342 | 22.8 | 90 | 90 | 250 | 50 | 150
3x50Al GPLK 10.5 | 50 Al |  | 10 | 0 | 0.713 | 0.089 | 0.28 | 0.003 | 1.48 | 1.57 | 0.14 | 83 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 4.25 | 45 | 50 | 160 | 50 | 168

## Trafo
Name | Shortname | Unom1 | Unom2 | Snom | uk | Pk | Pnul | Inul | R0 | Z0 | Side Z0 | Ik2s | s1 | s2 | Clock | Tapside | Tapsize | Tapmin | Tapnom | Tapmax | Ki | Tau | Controllable
|  | kV | kV | MVA | % | kW | kW | A | Ohm | Ohm |  | kA |  |  |  |  | kV |  |  |  |  | s
32MVA AEG |  | 150 | 11 | 40 | 17.5 | 196 | 34.3 | 20.9946 | 0.014081 | 0.50291 | 0 | 11.9969 | Y | D | 5 | 1 | 2.5 | -13 | 0 | 9 | 0 | 0 | FALSE
28MVA SMIT |  | 150 | 11 | 40 | 18 | 222 | 23.1 | 20.9946 | 3.7 | 98.57 | 0 | 11.6636 | Y | D | 5 | 1 | 2.5 | -13 | 0 | 9 | 0 | 0 | FALSE
60MVA SMIT |  | 150 | 52.5 | 60 | 20.1 | 221 | 18.6 | 6.5983 | 0.16074 | 8.7718 | 0 | 3.2827 | Y | D | 5 | 1 | 2.5 | -9 | 0 | 10 | 0 | 0 | FALSE
60MVA TIRONI |  | 150 | 52.5 | 60 | 20.1 | 197 | 18.2 | 6.5983 | 0.14329 | 8.7718 | 0 | 3.2827 | YN | D | 5 | 1 | 2.5 | -9 | 0 | 9 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.68 | 4.6 | 0.43 | 5.7735 | 0.00437 | 0.013984 | 0 | 15.6889 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.72 | 4.6 | 0.43 | 5.7735 | 0.00437 | 0.014136 | 0 | 15.5202 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.14 | 4.6 | 0.43 | 5.7735 | 0.00437 | 0.015732 | 0 | 13.9457 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.63 | 4.11 | 6.5 | 0.6 | 9.0933 | 0.0024893 | 0.0099162 | 0 | 22.1247 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 4.01 | 4.6 | 0.43 | 5.7735 | 0.00437 | 0.015238 | 0 | 14.3978 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/315 kVA Smit |  | 10.5 | 0.4 | 0.315 | 3.59 | 3.1 | 0.43 | 4.5466 | 0.0047488 | 0.017323 | 0 | 12.6647 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.81 | 1.905 | 0.26 | 2.3094 | 0.011311 | 0.036195 | 0 | 6.0614 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA SBG |  | 10.5 | 0.4 | 0.16 | 4 | 1.905 | 0.26 | 2.3094 | 0.011311 | 0.038 | 0 | 5.7735 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 3.9 | 3.75 | 0.515 | 5.7735 | 0.0035625 | 0.01482 | 0 | 14.8039 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA SBG |  | 10.5 | 0.4 | 0.63 | 4.1 | 6.5 | 0.6 | 9.0933 | 0.0024893 | 0.0098921 | 0 | 22.1787 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.81 | 3.75 | 0.515 | 5.7735 | 0.0035625 | 0.014478 | 0 | 15.1536 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.99 | 2.64 | 0.365 | 3.6084 | 0.0064205 | 0.024259 | 0 | 9.0437 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 3.9 | 3.75 | 0.515 | 5.7735 | 0.0035625 | 0.01482 | 0 | 14.8039 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.91 | 2.64 | 0.365 | 3.6084 | 0.0064205 | 0.023773 | 0 | 9.2287 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9500/400 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.03 | 6.5 | 0.6 | 9.0933 | 0.0024893 | 0.0097232 | 0 | 22.5639 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.67 | 5.2 | 0.745 | 9.0933 | 0.0019914 | 0.0088546 | 0 | 24.7773 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.57 | 5.2 | 0.745 | 9.0933 | 0.0019914 | 0.0086133 | 0 | 25.4713 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 4.02 | 5.2 | 0.745 | 9.0933 | 0.0019914 | 0.0096991 | 0 | 22.6201 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.1 | 3.75 | 0.515 | 5.7735 | 0.0035625 | 0.01558 | 0 | 14.0817 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.95 | 3.25 | 0.3 | 3.6084 | 0.007904 | 0.024016 | 0 | 9.1353 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.19 | 3.75 | 0.515 | 5.7735 | 0.0035625 | 0.015922 | 0 | 13.7792 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.92 | 3.25 | 0.3 | 3.6084 | 0.007904 | 0.023834 | 0 | 9.2052 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.69 | 3.325 | 0.405 | 5.7735 | 0.0031588 | 0.017822 | 0 | 12.3102 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.15 | 3.325 | 0.405 | 5.7735 | 0.0031588 | 0.01577 | 0 | 13.9121 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SGB |  | 10.5 | 0.4 | 0.25 | 4.2 | 2.46 | 0.3 | 3.6084 | 0.0059827 | 0.025536 | 0 | 8.5915 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.99 | 3.325 | 0.405 | 5.7735 | 0.0031588 | 0.015162 | 0 | 14.4699 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4 | 5 | 0.545 | 9.0933 | 0.0019148 | 0.0096508 | 0 | 22.7332 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA ELTAS |  | 10.5 | 0.4 | 0.4 | 4.31 | 4.6 | 0.43 | 5.7735 | 0.00437 | 0.016378 | 0 | 13.3956 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4.1 | 3.325 | 0.405 | 5.7735 | 0.0031588 | 0.01558 | 0 | 14.0817 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.1 | 3.25 | 0.3 | 3.6084 | 0.007904 | 0.024928 | 0 | 8.8011 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.71 | 4.6 | 0.43 | 5.7735 | 0.00437 | 0.014098 | 0 | 15.562 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.04 | 3.25 | 0.3 | 3.6084 | 0.007904 | 0.024563 | 0 | 8.9318 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.69 | 6.5 | 0.6 | 9.0933 | 0.0024893 | 0.0089029 | 0 | 24.643 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA SBG |  | 10.5 | 0.4 | 0.63 | 4.2 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.75 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.79 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA EFACEC |  | 10.5 | 0.4 | 0.4 | 4.1 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SBG |  | 10.5 | 0.4 | 0.25 | 4 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.68 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA EFACEC |  | 10.5 | 0.4 | 0.63 | 4.1 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.41 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.85 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.9 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.76 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4.1 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.13 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.85 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.07 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.92 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA LAP |  | 10.5 | 0.4 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SBG |  | 10.5 | 0.4 | 0.25 | 3.9 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.93 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4.2 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/315 kVA IEO |  | 10.5 | 0.4 | 0.315 | 3.47 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.02 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.91 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 4 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.06 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.4 | 3.9 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.02 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA EFACEC |  | 10.5 | 0.4 | 0.4 | 4.2 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.63 | 4.05 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.09 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SBG |  | 10.5 | 0.4 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.25 | 3.92 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA EATON |  | 10.5 | 0.4 | 0.4 | 4.08 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.4 | 3.95 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.63 | 4.03 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.55 | 1.75 | 0.145 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.08 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA EFACEC |  | 10.5 | 0.4 | 0.63 | 4 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SBG |  | 10.5 | 0.4 | 0.25 | 4.2 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.31 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA ELTAS |  | 10.5 | 0.4 | 0.25 | 3.97 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA ELTAS |  | 10.5 | 0.4 | 0.25 | 3.88 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA ELTAS |  | 10.5 | 0.4 | 0.4 | 4.2 | 0.003182 | 0.000379 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA ELTAS |  | 10.5 | 0.4 | 0.4 | 4.31 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA ELTAS |  | 10.5 | 0.4 | 0.25 | 3.08 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.1 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Onbekend |  | 10.5 | 0.4 | 0.4 | 4 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.94 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.83 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 4.15 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.93 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/150 kVA Smit |  | 10.5 | 0.4 | 0.15 | 3.58 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.63 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/85 kVA Smit |  | 10.5 | 0.4 | 0.085 | 3.59 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.98 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.69 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.94 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.84 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.87 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.98 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.55 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.89 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.92 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.72 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.42 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.09 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Pauwels |  | 10.5 | 0.4 | 0.1 | 4.01 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.87 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9500/380 V/150 kVA Smit |  | 10.5 | 0.4 | 0.15 | 3.48 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.69 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.08 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.1 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/150 kVA Smit |  | 10.5 | 0.4 | 0.15 | 3.45 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9750/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.07 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA HOLEC |  | 10.5 | 0.4 | 0.25 | 3.99 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.62 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.58 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA ELTAS |  | 10.5 | 0.4 | 0.4 | 4.12 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.92 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.48 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.93 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.6 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 4.13 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.09 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/380 V/200 kVA IEO |  | 10.5 | 0.4 | 0.2 | 3.93 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.04 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 7 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA EATON |  | 10.5 | 0.4 | 0.63 | 4.15 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.91 | 1.35 | 0.21 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/315 kVA IEO |  | 10.5 | 0.4 | 0.315 | 3.45 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.75 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.62 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA SBG |  | 10.5 | 0.4 | 0.16 | 4 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.94 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.96 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.65 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.6 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.86 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SGB |  | 10.5 | 0.4 | 0.25 | 4 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.95 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.56 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.66 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.96 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.97 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.5 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 4.02 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 4 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.5 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.57 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.83 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.41 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.73 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/630 kVA Smit |  | 10.5 | 0.4 | 0.63 | 3.89 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/315 kVA IEO |  | 10.5 | 0.4 | 0.315 | 3.46 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.33 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.72 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.47 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.91 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.17 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.89 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 3.57 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 4.1 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/75 kVA Smit |  | 10.5 | 0.4 | 0.075 | 3.42 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.82 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 4 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.69 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.57 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.58 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 4.12 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.15 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.89 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.75 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.86 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.52 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 4 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.73 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/400 V/250 kVA HOLEC |  | 10.5 | 0.4 | 0.25 | 4.1 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.56 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.11 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.98 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.04 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.53 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Lepper-Dominit |  | 10.5 | 0.4 | 0.25 | 3.96 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.61 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.7 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 4.11 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/200 kVA IEO |  | 10.5 | 0.4 | 0.2 | 3.5 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.02 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.51 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.86 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA HOLEC |  | 10.5 | 0.4 | 0.1 | 3.96 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 3.9 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.19 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | -1 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA SBG |  | 10.5 | 0.4 | 0.16 | 3.9 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/400 kVA SGB |  | 10.5 | 0.4 | 0.4 | 4.2 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/400 kVA SGB |  | 10.5 | 0.4 | 0.4 | 4.1 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/100 kVA SGB |  | 10.5 | 0.4 | 0.1 | 3.9 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/250 kVA SGB |  | 10.5 | 0.4 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.1 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.82 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA SBG |  | 10.5 | 0.4 | 0.16 | 3.8 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/100 kVA Pauwels |  | 10.5 | 0.4 | 0.1 | 3.98 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/100 kVA Pauwels |  | 10.5 | 0.4 | 0.1 | 4 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.91 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/ 250 kVA SBG |  | 10.5 | 0.4 | 0.25 | 3.8 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.92 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.41 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.64 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.6 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 4.01 | 1.83 | 0.23 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.08 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA DOM |  | 10.5 | 0.4 | 0.25 | 3.9 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.69 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.96 | 1.185 | 0.172 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.92 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.82 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.72 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.11 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.94 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Lepper-Dominit |  | 10.5 | 0.4 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.11 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.92 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA IEO |  | 10.5 | 0.4 | 0.1 | 4.01 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA ACEC |  | 10.5 | 0.4 | 0.25 | 4.05 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.3 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/50 kVA Smit |  | 10.5 | 0.4 | 0.05 | 3.34 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.05 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.56 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.98 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.92 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.88 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 3.85 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.97 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4.2 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.11 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.65 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SGB |  | 10.5 | 0.4 | 0.25 | 3.9 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/150 kVA Smit |  | 10.5 | 0.4 | 0.15 | 3.49 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.48 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA SGB |  | 10.5 | 0.4 | 0.63 | 3.9 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.01 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/400 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.03 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9500/380 V/600 kVA Smit |  | 10.5 | 0.4 | 0.6 | 3.53 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.43 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.83 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.84 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 4.02 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.78 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 4.06 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.78 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.06 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Lepper-Dominit |  | 10.5 | 0.4 | 0.25 | 4.05 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SGB |  | 10.5 | 0.4 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.79 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.96 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.88 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.79 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9500/380 V/315 kVA IEO |  | 10.5 | 0.4 | 0.315 | 3.43 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.78 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.17 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.66 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.76 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.81 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.98 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.94 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.52 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.87 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.99 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/400 kVA SGB |  | 10.5 | 0.4 | 0.4 | 3.9 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.65 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 4.13 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.86 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.85 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.93 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.92 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.99 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.95 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/315 kVA IEO |  | 10.5 | 0.4 | 0.315 | 3.64 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.57 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.79 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/630 kVA Smit |  | 10.5 | 0.4 | 0.63 | 4.05 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/380 V/300 kVA IEO |  | 10.5 | 0.4 | 0.3 | 3.59 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4.1 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.01 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.95 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/380 V/630 kVA Smit |  | 10.5 | 0.4 | 0.63 | 3.99 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.01 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9500/380 V/315 kVA Smit |  | 10.5 | 0.4 | 0.315 | 3.4 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.07 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.66 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.9 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.96 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/630 kVA SGB |  | 10.5 | 0.4 | 0.63 | 3.9 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.7 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/630 kVA Smit |  | 10.5 | 0.4 | 0.63 | 3.94 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.94 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA SGB |  | 10.5 | 0.4 | 0.25 | 4.1 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.06 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.96 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.89 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.84 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA SGB |  | 10.5 | 0.4 | 0.63 | 4 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 3.8 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.23 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.81 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.77 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9500/380 V/315 kVA IEO |  | 10.5 | 0.4 | 0.315 | 4.15 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.07 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.94 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/50 kVA Smit |  | 10.5 | 0.4 | 0.05 | 3.46 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.98 | 1.83 | 0.23 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.05 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.9 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.71 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.08 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Lepper-Dominit |  | 10.5 | 0.4 | 0.25 | 3.8 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 3.8 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA SBG |  | 10.5 | 0.4 | 0.4 | 4 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.87 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 3.91 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.06 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/400 kVA SGB |  | 10.5 | 0.4 | 0.4 | 4 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.69 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.8 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA Pauwels |  | 10.5 | 0.4 | 0.16 | 3.81 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.56 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 4.01 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.19 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.94 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.58 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4.12 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.98 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.61 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.69 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.96 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/800 kVA Pauwels |  | 10.5 | 0.4 | 0.8 | 5.63 | 8.8 | 0.97 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 3.91 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.6 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 3.87 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.62 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.7 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.95 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.16 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.15 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.84 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.15 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9750/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 4.08 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 1 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.4 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.97 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/400 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.57 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.72 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.68 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.07 | 5 | 0.545 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.97 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/160 kVA Smit |  | 10.5 | 0.4 | 0.16 | 3.93 | 1.83 | 0.23 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.24 | 0.003179 | 0.000354 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.18 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.08 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.14 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.15 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/160 kVA SBG |  | 10.5 | 0.4 | 0.16 | 4 | 1.83 | 0.23 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA SGB |  | 10.5 | 0.4 | 0.63 | 4.1 | 5 | 0.545 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.25 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.87 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/1000 kVA IEO |  | 10.5 | 0.4 | 1 | 6.17 | 7.475 | 0.695 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA SGB |  | 10.5 | 0.4 | 0.63 | 4.2 | 5 | 0.545 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/380 V/300 kVA IEO |  | 10.5 | 0.4 | 0.3 | 3.56 | 3.1 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.97 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.83 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/400 kVA Pauwels |  | 10.5 | 0.4 | 0.4 | 3.79 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA ABB |  | 10.5 | 0.4 | 0.4 | 3.91 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA ELTAS |  | 10.5 | 0.4 | 0.25 | 3.87 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA KONCAR D&ST |  | 10.5 | 0.4 | 0.25 | 3.82 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA ELTAS |  | 10.5 | 0.4 | 0.25 | 3.94 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA EATON |  | 10.5 | 0.4 | 0.25 | 3.88 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA ELTAS |  | 10.5 | 0.4 | 0.25 | 3.92 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA KYTE Powertech |  | 10.5 | 0.4 | 0.4 | 3.87 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.68 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA EATON |  | 10.5 | 0.4 | 0.63 | 4.34 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.26 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA EATON |  | 10.5 | 0.4 | 0.4 | 4.2 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.3 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 4.01 | 1.185 | 0.172 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.11 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.65 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.01 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.91 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.88 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.94 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.97 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.95 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4.2 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.18 | 5 | 0.545 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.15 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.99 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 4 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.01 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 3.89 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.74 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.93 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4.1 | 5 | 0.545 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.94 | 2.46 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.88 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.85 | 3.325 | 0.405 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.88 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.8 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.94 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.04 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.05 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA Smit |  | 10.5 | 0.4 | 0.25 | 4.09 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.86 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.96 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.03 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.02 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
9750/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.54 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.8 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.5 | 0.4 | 0.1 | 3.37 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/380 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.63 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 4 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/420 V/250 kVA Pauwels |  | 10.5 | 0.4 | 0.25 | 3.91 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.71 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA Pauwels |  | 10.5 | 0.4 | 0.63 | 3.85 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.81 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 4.11 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.83 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/ 250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 4.02 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 3.94 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10500/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.89 | 5.2 | 0.745 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/400 kVA Smit |  | 10.5 | 0.4 | 0.4 | 4.19 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10000/400 V/200 kVA Smit |  | 10.5 | 0.4 | 0.2 | 3.59 | 2.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.5 | 0.4 | 0.25 | 3.99 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10250/400 V/160 kVA IEO |  | 10.5 | 0.4 | 0.16 | 4 | 1.905 | 0.26 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.88 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 4 | 5 | 0.545 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/630 kVA IEO |  | 10.5 | 0.4 | 0.63 | 3.68 | 6.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.71 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/400 kVA IEO |  | 10.5 | 0.4 | 0.4 | 3.77 | 4.6 | 0.43 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
10750/420 V/250 kVA EFACEC |  | 10.5 | 0.4 | 0.25 | 4.2 | 3.25 | 0.3 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 3 | 3 | 3 | 0 | 0 | FALSE
Norm 400 kVA | 400 KVA | 10.75 | 0.42 | 0.4 | 4 | 3.75 | 0.515 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 5 | 3 | 1 | 0 | 0 | FALSE
10500/420 V/250 kVA IEO |  | 10.5 | 0.42 | 0.25 | 4.07 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 5 | 3 | 1 | 0 | 0 | FALSE
10250/400 V/100 kVA Smit |  | 10.25 | 0.4 | 0.1 | 3.9 | 1.35 | 0.19 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 5 | 3 | 1 | 0 | 0 | FALSE
10750/420 V/250 kVA IEO |  | 10.75 | 0.42 | 0.25 | 3.97 | 2.64 | 0.365 | 0 | 0 | 0 | 0 | 0 | D | YN | 5 | 1 | 0.25 | 5 | 3 | 1 | 0 | 0 | FALSE

## Specialtrafo
Name | Sort | Shortname | Unom1 | Unom2 | Snom | ukmin | uknom | ukmax | Pkmin | Pknom | Pkmax | Pnul | Inul | R0 | Z0 | Ik2s | Tapside | Tapsize | Tapmin | Tapnom | Tapmax | Ki | Tau
|  |  | kV | kV | MVA | % | % | % | kW | kW | kW | kW | A | Ohm | Ohm | kA |  | kV |  |  |  |  | s
10500 V/23 MVA Smit | BOOSTER | 23 MVA | 10.5 | 10.5 | 23 | 0.45 | 0.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019 | 19 | 1 | 0.15 | 1 | 7 | 13 | 0 | 0

## Coil
Name | Shortname | Unom | Inom | R | X | R0 | X0 | R2 | X2 | Ik2s
|  | kV | A | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | kA
320.0A Smit BS 970 B/18 0.30Ohm 10.0kV 0.00Ohm |  | 10 | 320 | 0 | 0.3 | 0 | 0.3 | 0 | 0.3 | 14.1
320.0A SMIT DSKS10 0.34Ohm 12.0kV 0.00Ohm |  | 12 | 320 | 0 | 0.34 | 0 | 0.34 | 0 | 0.34 | 16.5
400.0A ALSTOM ACR 0.87Ohm 12.0kV 0.00Ohm |  | 12 | 400 | 0 | 0.87 | 0 | 0.87 | 0 | 0.87 | 7
600.0A NOKIAN XKSP 0.60Ohm 12.0kV 0.00Ohm |  | 12 | 600 | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0

## 3wt
Name | Unom1 | Unom2 | Unom3 | Snom1 | Snom2 | Snom3 | uk12 | uk13 | uk23 | Pk12 | Pk13 | Pk23 | Sat12 | Sat13 | Sat23 | Pnul | Inul | R012 | Z012 | R013 | Z013 | R023 | Z023 | Ik2s1 | Ik2s2 | Ik2s3 | s1 | s2 | s3 | Clock12 | Clock13 | Tapside_u | Tapsize_u | Tapmin_u | Tapnom_u | Tapmax_u | Tapside_i | Tapsize_i | Tapmin_i | Tapnom_i | Tapmax_i
| kV | kV | kV | MVA | MVA | MVA | % | % | % | kW | kW | kW | MVA | MVA | MVA | kW | A | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | kA | kA | kA | [6 empty] | kV |  |  |  |  | kV
30MVA SMIT | 150 | 52.5 | 11.25 | 40 | 40 | 30 | 12 | 18 | 5.1 | 133 | 139 | 110 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Y | D | D | 5 | 5 | 1 | 2.5 | -11 | 0 | 11 | 2 | 0 | 0 | 0 | 0

## Rail
Name | Unom | Inom | Ik_dynamic | Ik_thermic | T_thermic
| kV | A | kA | kA | s
ALUMINIUM-BUIS - 150.0kV | 150 | 3000 | 100 | 40 | 3
ONBEKEND - | 0 | 0 | 0 | 0 | 0
Xiria 24kV 630A | 24 | 630 | 40 | 20 | 3
Magnefix MD4 12kV 400A | 12 | 400 | 30 | 14.4 | 1
Magnefix MF 12kV 450A | 12 | 450 | 30 | 20 | 1
SafePlus 24kV 630A | 24 | 630 | 22 | 8.6 | 3
Xiria 12kV 630A | 12 | 630 | 50 | 20 | 3
SafePlus 24kV 0A | 24 | 400 | 30 | 14.4 | 1
Magnefix MF 12kV 400A | 12 | 400 | 50 | 20 | 1
Xiria-E 24kV 630A | 24 | 630 | 40 | 20 | 3
8DJH Compact 24kV 630A | 24 | 630 | 30 | 14.4 | 1
Traditioneel 10kV 0A | 10.5 | 250 | 22 | 8.6 | 3
Magnefix MF 10kV 630A | 10.5 | 630 | 50 | 20 | 1
Magnefix MF 10kV 400A | 10.5 | 400 | 50 | 20 | 1
Prefab laag 10kV 0A | 10.5 | 400 | 22 | 8.6 | 3
Magnefix MD4 T 12kV 400A | 12 | 400 | 30 | 14.4 | 1
Prefab hoog 10kV 0A | 10.5 | 400 | 22 | 8.6 | 3
SVS 08 12kV 800A | 12 | 800 | 50 | 20 | 2.5
Prefab hoog 10kV 630A | 10.5 | 630 | 22 | 8.6 | 3
Prefab hoog 10kV 400A | 10.5 | 400 | 22 | 8.6 | 3
Comb PH + TR 10kV 0A | 10.5 | 400 | 30 | 14.4 | 1
Magnefix MD4 12kV 0A | 12 | 400 | 30 | 14.4 | 1
Magnefix MD4 12kV 630A | 12 | 630 | 30 | 14.4 | 1
SVS 12 12kV 1250A | 12 | 1250 | 50 | 20 | 2.5
Prefab laag 10kV 360A | 10 | 360 | 30 | 14.4 | 1
Univer-G 12kV 1250A | 12 | 1250 | 22 | 8.6 | 3
Traditioneel 10kV 3000A | 10 | 3000 | 22 | 8.6 | 3
Capitole HC 12kV 0A | 12 | 1000 | 50 | 40 | 3
BA-BD 12kV 3000A | 12 | 3000 | 125 | 50 | 3
Capitole IC6 10kV 0A | 10.5 | 2000 | 50 | 20 | 2.5
Magnefix MD4 12kV 250A | 12 | 250 | 30 | 14.4 | 1
Magnefix MD4 12kV 310A | 12 | 310 | 30 | 14.4 | 1
NES-H 12kV 2500A | 12 | 2500 | 125 | 50 | 3
NES-H 12kV 1250A | 12 | 1250 | 125 | 50 | 3
SVS 06 12kV 630A | 12 | 630 | 50 | 20 | 2.5
Magnefix MF 10kV 1000A | 10.5 | 1000 | 50 | 20 | 1
Magnefix MD4 12kV 450A | 12 | 450 | 30 | 14.4 | 1
8DJH Compact 24kV 0A | 24 | 400 | 30 | 14.4 | 1
Magnefix MF 10kV 450A | 10.5 | 450 | 50 | 20 | 1
Magnefix MD4 12kV 420A | 12 | 420 | 30 | 14.4 | 1

## Sg
Name | Unom | Snom | Cosnom | Qmin | Qmax | rg | xd"sat | Excitation | Rotor | IkP | Ufmax | Xdsat | Xl | Xd | Xq | X0 | Xd' | Xq' | Xd'' | Xq'' | Open circuit time constant | Td' | Tq' | Td'' | Tq'' | Inertia as J | H | J | KD | nnom | Tdc unknown | Tdc | Ikd
| kV | MVA |  | Mvar | Mvar | pu | pu |  |  | kA | pu | pu | pu | pu | pu | pu | pu | pu | pu | pu |  | s | s | s | s |  | s | kgm² | pu | omw/min |  | A | kA

## Sm
Name | Unom | Snom | Cosnom | rg | xd"sat | Ia/Inom | R/Xa | Rotor | IkP | Xl | Xd | Xq | X0 | Xd' | Xq' | Xq'' | Open circuit time constant | Td' | Tq' | Td'' | Tq'' | H | KD | Tdc unknown | Tdc
| kV | MVA |  | pu | pu |  |  |  | kA | pu | pu | pu | pu | pu | pu | pu |  | s | s | s | s | s | pu |  | A

## Asg
Name | Unom | Pnom | Ia/Inom | Poles | Revs | Kipp | R/X | Cosnom | p2 | Cos2 | p3 | Cos3 | p4 | Cos4 | p5 | Locked rotor torque | Kipp revs | Efficiency | Inertia | k2 | k1 | k0 | Double cage | Own parameters | TMECHCHARENABLE | TELCHARENABLE | Rs | Xsl | Xm | Rr | Xrl | Rr2 | Xr2l
| kV | MW |  |  | /min | % |  |  | pu |  | pu |  | pu |  | pu | % | /min | % | /kgm² | % | % | % |  |  |  |  | pu | pu | pu | pu | pu | pu | pu

## Asm
Name | Unom | Pnom | Ia/Inom | Poles | Revs | Kipp | R/X | Cosnom | Effnom | p2 | Cos2 | Eff2 | p3 | Cos3 | Eff3 | p4 | Cos4 | Eff4 | p5 | Cos5 | Eff5 | OnePhase | Locked rotor torque | Kipp revs | Inertia | k2 | k1 | k0 | Double cage | Own parameters | TmechCharEnable | TelCharEnable | Rs | Xsl | Xm | Rr | Xrl | Rr2 | Xr2l
| kV | MW |  |  | /min | % |  |  | % | pu |  | % | pu |  | % | pu |  | % | pu |  | % |  | % | /min | /kgm² | % | % | % |  |  |  |  | pu | pu | pu | pu | pu | pu | pu

## Zigzag
Name | R0 | X0
| Ohm | Ohm

## Wind
Name | Unom | Pnom | Ik/Inom | R/X | WindCutIn | WindNom | WindCuttingOut | WindCuttedOut
| kV | MW |  |  | m/s | m/s | m/s | m/s

## Switch
Name | Shortname | Unom | Inom | Ik_make | Ik_dynamic | Ik_thermic | T_thermic
|  | kV | A | kA | kA | kA | s
24.0kV Xiria SVR14BA-2406 EATON LS Motor 630A |  | 24 | 630 | 0 | 0 | 16 | 1
12.0kV MD4 EATON LS Hand 400A |  | 12 | 400 | 0 | 0 | 14.4 | 0
24.0kV Xiria SVR14BA-2406 EATON LS Hand 630A |  | 24 | 630 | 0 | 0 | 20 | 1
12.0kV MF EATON LS 450A |  | 12 | 450 | 0 | 0 | 0 | 0
24.0kV SafePlus-SF6 Omschak. ABB LS Hand 200A |  | 24 | 200 | 0 | 50 | 21 | 3
24.0kV SafePlus-SF6 Omschak. ABB LS Hand 630A |  | 24 | 630 | 0 | 50 | 21 | 3
24.0kV SafePlus-SF6 Omschak. ABB LS Motor 630A |  | 24 | 630 | 0 | 50 | 21 | 3
12.0kV Xiria SVR14BA-1206 EATON LS Hand 630A |  | 12 | 630 | 0 | 0 | 20 | 1
12.0kV MD4 HOLEC LS Hand 400A |  | 12 | 400 | 0 | 0 | 14.4 | 1
24.0kV 8DJH-SF6 Siemens LS Hand 630A |  | 24 | 630 | 0 | 50 | 20 | 1
24.0kV 8DJH-SF6 Siemens LS Hand 200A |  | 24 | 200 | 0 | 50 | 20 | 1
12.0kV LS Hapam LS Hand 400A |  | 12 | 400 | 0 | 0 | 0 | 0
10.5kV LS HOLEC LS Hand |  | 10.5 | 0 | 0 | 0 | 0 | 0
12.0kV LS Onbekend LS Hand 400A |  | 12 | 400 | 0 | 0 | 0 | 0
12.0kV LS Driescher LS Hand 400A |  | 12 | 400 | 0 | 0 | 0 | 0
10.5kV MF HOLEC LS Hand 450A |  | 10.5 | 450 | 0 | 0 | 0 | 0
12.0kV CF Siemens LS Hand 400A |  | 12 | 400 | 0 | 0 | 0 | 0
10.5kV LS Onbekend LS Hand |  | 10.5 | 0 | 0 | 0 | 0 | 0
10.5kV SVS HOLEC LS Hand 630A |  | 10.5 | 630 | 0 | 0 | 0 | 0
10.5kV Magnefix HOLEC LS Hand 400A |  | 10.5 | 400 | 0 | 0 | 0 | 0
12.0kV LS Siemens LS Hand 400A |  | 12 | 400 | 0 | 0 | 0 | 0
10.5kV SVS HOLEC LS Hand |  | 10.5 | 0 | 0 | 0 | 0 | 0
12.0kV SVS 06 EATON LS Hand 630A |  | 12 | 630 | 0 | 0 | 0 | 0
10.5kV HC IC6-6 HOLEC LS Hand 630A |  | 10.5 | 630 | 0 | 0 | 0 | 0
12.0kV SVS 08 EATON LS Hand |  | 12 | 0 | 0 | 0 | 0 | 0
10.5kV Onbekend Onbekend LS Hand |  | 10.5 | 0 | 0 | 0 | 0 | 0
10.5kV HC ICS6 HOLEC LS Hand 400A |  | 10.5 | 400 | 0 | 0 | 0 | 0
12.0kV Xiria EATON LS Hand 630A |  | 12 | 630 | 0 | 0 | 0 | 0
24.0kV Xiria SVR14AA-2406 EATON LS Motor 630A |  | 24 | 630 | 0 | 0 | 16 | 1
12.0kV NAL 12-12K ABB LS 1250A |  | 12 | 1250 | 0 | 0 | 31.5 | 1
12.0kV SVS 08 EATON LS Hand 630A |  | 12 | 630 | 0 | 0 | 0 | 0
12.0kV MD4 HOLEC LS Hand 400A |  | 12 | 400 | 0 | 31 | 14.4 | 1

## Fuse
Name | Shortname | Unom | Inom | Threephase | I1 | T1 | I2 | T2 | I3 | T3 | I4 | T4 | I5 | T5 | I6 | T6 | I7 | T7 | I8 | T8 | I9 | T9 | I10 | T10 | I11 | T11 | I12 | T12 | I13 | T13 | I14 | T14 | I15 | T15 | I16 | T16
|  | kV | A |  | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s
50A Full Range | Flr 50 A | 10 | 50 | FALSE | 104 | 1000 | 131 | 500 | 172 | 200 | 217 | 100 | 276 | 50 | 343 | 20 | 383 | 10 | 413 | 5 | 450 | 2 | 480 | 1 | 500 | 0.5 | 525 | 0.2 | 567 | 0.1 | 633 | 0.05 | 750 | 0.02 | 850 | 0.01
31.5A Full Range | Flr 31.5 A | 10 | 31.5 | FALSE | 72.5 | 1000 | 86.2 | 500 | 108 | 200 | 129 | 100 | 154 | 50 | 189 | 20 | 222 | 10 | 250 | 5 | 275 | 2 | 294 | 1 | 300 | 0.5 | 320 | 0.2 | 330 | 0.1 | 340 | 0.05 | 367 | 0.02 | 425 | 0.01
20A Full Range | Flr 20 A | 10 | 20 | FALSE | 48.5 | 1000 | 58 | 500 | 71.2 | 200 | 84.9 | 100 | 103 | 50 | 124 | 20 | 140 | 10 | 150 | 5 | 168 | 2 | 178 | 1 | 182 | 0.5 | 182 | 0.2 | 186 | 0.1 | 186 | 0.05 | 193 | 0.02 | 208 | 0.01
16A Full range | Flr 16 A | 10 | 16 | FALSE | 39.4 | 1000 | 47.8 | 500 | 57.4 | 200 | 67 | 100 | 79.2 | 50 | 93 | 20 | 105 | 10 | 120 | 5 | 135 | 2 | 138 | 1 | 144 | 0.5 | 144 | 0.2 | 145 | 0.1 | 146 | 0.05 | 149 | 0.02 | 157 | 0.01
10A Full range | Flr 10 A | 10 | 10 | FALSE | 27.6 | 1000 | 32.7 | 500 | 39.2 | 200 | 44.2 | 100 | 49.7 | 50 | 56.6 | 20 | 63 | 10 | 69 | 5 | 73 | 2 | 77 | 1 | 80 | 0.5 | 83 | 0.2 | 86 | 0.1 | 88 | 0.05 | 90 | 0.02 | 98 | 0.01
25A Full Range | Flr 25 A | 10 | 25 | FALSE | 59.5 | 1000 | 70.4 | 500 | 87.1 | 200 | 104 | 100 | 125 | 50 | 152 | 20 | 175 | 10 | 200 | 5 | 225 | 2 | 240 | 1 | 247 | 0.5 | 250 | 0.2 | 250 | 0.1 | 256 | 0.05 | 275 | 0.02 | 300 | 0.01
63A Full Range | Flr 63 A | 10 | 63 | FALSE | 133 | 1000 | 164 | 500 | 221 | 200 | 278 | 100 | 355 | 50 | 455 | 20 | 525 | 10 | 575 | 5 | 616 | 2 | 644 | 1 | 666 | 0.5 | 710 | 0.2 | 775 | 0.1 | 845 | 0.05 | 975 | 0.02 | 1188 | 0.01
40A Full range | Flr 40 A | 10 | 40 | FALSE | 93.3 | 1000 | 112 | 500 | 138 | 200 | 166 | 100 | 199 | 50 | 240 | 20 | 275 | 10 | 320 | 5 | 350 | 2 | 383 | 1 | 400 | 0.5 | 418 | 0.2 | 427 | 0.1 | 450 | 0.05 | 500 | 0.02 | 570 | 0.01
80A Full range | Flr 80 A | 10 | 80 | FALSE | 175 | 1000 | 214 | 500 | 283 | 200 | 353 | 100 | 453 | 50 | 576 | 20 | 670 | 10 | 740 | 5 | 800 | 2 | 840 | 1 | 865 | 0.5 | 900 | 0.2 | 980 | 0.1 | 1095 | 0.05 | 1313 | 0.02 | 1500 | 0.01
31.5A 12.0kV | 31.5 A | 12 | 31.5 | FALSE | 51 | 1000 | 55 | 500 | 62 | 200 | 68 | 100 | 76 | 50 | 92 | 20 | 120 | 10 | 130 | 5 | 175 | 2 | 220 | 1 | 275 | 0.5 | 380 | 0.2 | 440 | 0.1 | 540 | 0.05 | 725 | 0.02 | 925 | 0.01
20.0A 12.0kV | 20 A | 12 | 20 | FALSE | 48.5 | 1000 | 58 | 500 | 71.2 | 200 | 84.9 | 100 | 103 | 50 | 124 | 20 | 140 | 10 | 150 | 5 | 168 | 2 | 178 | 1 | 182 | 0.5 | 182 | 0.2 | 186 | 0.1 | 186 | 0.05 | 193 | 0.02 | 208 | 0.01
10.0A 12.0kV | 10 A | 12 | 10 | FALSE | 18.2 | 1000 | 19.6 | 500 | 22.2 | 200 | 25.1 | 100 | 29.3 | 50 | 37.1 | 20 | 42 | 10 | 52 | 5 | 64 | 2 | 71 | 1 | 80 | 0.5 | 90 | 0.2 | 99 | 0.1 | 110 | 0.05 | 135 | 0.02 | 150 | 0.01
63.0A 12.0kV | 63 A | 12 | 63 | FALSE | 133 | 1000 | 164 | 500 | 221 | 200 | 278 | 100 | 355 | 50 | 455 | 20 | 525 | 10 | 575 | 5 | 616 | 2 | 644 | 1 | 666 | 0.5 | 710 | 0.2 | 775 | 0.1 | 845 | 0.05 | 975 | 0.02 | 1188 | 0.01

## Breaker
Name | Shortname | Unom | Inom | Switchtime | Ik_make | Ik_break | Ik_dynamic | Ik_thermic | T_thermic
|  | kV | A | s | kA | kA | kA | kA | s
24.0kV Xiria NVR62BA-2402 EATON VS Hand 200A |  | 24 | 200 | 0.07 | 0 | 0 | 0 | 16 | 1
12.0kV MD4 NVX124A-1204 EATON VS Hand 400A |  | 12 | 400 | 0.07 | 0 | 0 | 0 | 14.4 | 1
24.0kV Xiria NVR62BA-2406 EATON VS Hand 630A |  | 24 | 630 | 0.07 | 0 | 0 | 0 | 16 | 0
24.0kV SafePlus-SF6 ABB VS Hand 630A |  | 24 | 630 | 0.07 | 0 | 0 | 0 | 16 | 3
12.0kV Xiria NVR62BA-1202 EATON VS Hand 200A |  | 12 | 200 | 0.07 | 0 | 0 | 0 | 20 | 0
10.5kV VS Onbekend VS |  | 10.5 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0
10.5kV A10/250/6 EIB VS Hand 630A |  | 10.5 | 630 | 0.07 | 0 | 0 | 0 | 20 | 3
10.5kV SVS 08 HOLEC VS Hand 630A |  | 10.5 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
10.5kV ESJ/10/6 Hapam VS 630A |  | 10.5 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
10.5kV SVS HOLEC VS Hand 630A |  | 10.5 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
12.0kV RMSG12-50-1250 ABB VS 1250A |  | 12 | 1250 | 0.07 | 0 | 0 | 0 | 0 | 0
12.0kV RMSG12-35-630 ABB VS 630A |  | 12 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
12.0kV DB10M400 BBC VS 1000A 400 |  | 12 | 1000 | 0.07 | 33.3333 | 0 | 57.5 | 23 | 5
12.0kV DB10M500 BBC VS 1200A 500 |  | 12 | 1200 | 0.07 | 41.6667 | 0 | 58 | 23 | 5
12.0kV NAL 12-12K ABB VS 1250A |  | 12 | 1250 | 0.07 | 0 | 0 | 0 | 31.5 | 1
12.0kV DB10P500 BBC VS 2500A 500 |  | 12 | 2500 | 0.07 | 41.6667 | 0 | 92 | 65 | 5
10.5kV Unitole 2116-1206 HOLEC VS 630A |  | 10.5 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
10.5kV HC HOLEC VS Hand |  | 10.5 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0
10.5kV Magnefix HOLEC VS Hand 400A |  | 10.5 | 400 | 0.07 | 0 | 0 | 0 | 0 | 0
12.0kV VD4 12.12.31 ABB VS 1250A |  | 12 | 1250 | 0.07 | 0 | 0 | 80 | 31.5 | 3
12.0kV VD4 12.06.20 ABB VS Motor 630A |  | 12 | 630 | 0.07 | 0 | 0 | 0 | 20 | 3
12.0kV VD4 12.12.20 ABB VS Motor 1250A |  | 12 | 1250 | 0.07 | 0 | 0 | 0 | 20 | 3
12.0kV SVS 06 EATON VS Hand 630A |  | 12 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
12.0kV SVS 08 EATON VS Hand |  | 12 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0
12.0kV SVS 08 EATON VS Hand 630A |  | 12 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
24.0kV Xiria NVR62BA-2406 EATON VS Motor 630A |  | 24 | 630 | 0.07 | 0 | 0 | 0 | 16 | 1
12.0kV Xiria NVR62BA-1206 EATON VS Hand 630A |  | 12 | 630 | 0.07 | 0 | 0 | 0 | 20 | 1
12.0kV Xiria EATON VS Hand 630A |  | 12 | 630 | 0.07 | 0 | 0 | 0 | 0 | 0
24.0kV Xiria NVR62BA-2405 EATON VS Motor 500A |  | 24 | 500 | 0.07 | 0 | 0 | 0 | 16 | 1
12.0kV DB10P400 BBC VS 2500A 400 |  | 12 | 2500 | 0.07 | 33.3333 | 0 | 92 | 72 | 5

## Current
Name | Shortname | Setting | Inom | I1 | T1 | I2 | T2 | I3 | T3 | I4 | T4 | I5 | T5 | I6 | T6 | I7 | T7 | I8 | T8 | I9 | T9 | I10 | T10 | I11 | T11 | I12 | T12 | I13 | T13 | I14 | T14 | I15 | T15 | I16 | T16 | I> | T> | I>> | T>> | I>>> | T>>> | Id | Ilt | Ist | m | Alfa | Beta | c | d | e | Uprop | Tinput | Toutput | Dropout | Treset | Resetmethod
|  |  | A | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s |  | A | A | [5 empty] | s |  | s | s |  | s
Schneider Electric P111 | 9021200-EL-M01-011-SB1 | 13 | 0 | [32 empty] | 1 |  | 0 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 9021200-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 6003597-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 6003597-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H3 | 9023416-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W3H3 | 9023416-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1000 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W3H3 | 9023416-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 40 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9023937-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 75 | 0.6 | 1504 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9023937-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 41 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003805-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003805-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9025020-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1200 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9025020-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9025020-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1200 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024707-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024707-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9025248-EL-M01-011-SB1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0.02 | 0.01
Schneider Electric P111 | 9025248-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004271-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 130 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004271-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 100 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024706-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024706-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024158-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024158-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024989-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 75 | 0.6 | 1000 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9024989-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9019853-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9019853-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9026658-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1120 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9026658-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9026464-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 130 | 0.6 | 1200 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9026464-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 40 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9027733-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1100 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9027733-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9025891-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 130 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9025891-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9025891-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 130 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9026115-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9026115-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 30 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9026115-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9026115-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 30 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9023463-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9023463-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003875-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 130 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003875-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003875-EL-M02-004-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003875-EL-M02-004-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SA82 | 0102181-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 720 | 1.2 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SA82 | 0102181-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 50 | 60 | 150 | 1.2 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102172-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1120 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102172-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102188-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1120 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102188-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 0101738-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 360 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 0101738-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 300 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 0101738-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 0101738-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 130 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 0101738-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 320 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 0101738-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 250 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102455-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1100 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102455-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102536-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102536-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0101376-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0101376-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 130 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102851-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1100 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102851-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 0102057-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 200 | 0.6 | 1200 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 0102057-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0105944-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1100 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0105944-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003436-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6005733-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 180 | 0.8 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6005853-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003794-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003839-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 170 | 1.3 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003839-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003877-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003877-EL-M02-002-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6005886-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 250 | 0.5 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003960-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003977-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 145 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SPRECHER & SCHUH MUT1 | 6005986-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 120 | 0.9 | 350 | 0.5 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6005986-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1000 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6005990-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 105 | 0.5 | 180 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6004215-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6004216-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 210 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIM1-H | 6004300-EL-M02-001-SB1 | 1 | 0 | [32 empty] | 210 | 0.9 | 1425 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6004301-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 0.86 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6004314-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6004340-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 200 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6004340-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6006110-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6006140-EL-M01-006-SB1 | 1 | 0 | [32 empty] | 110 | 0.6 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6006155-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 140 | 0.5 | 600 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6006168-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 90 | 0.5 | 240 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6006176-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 150 | 0.5 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6004352-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6007743-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 90 | 0.5 | 180 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6008319-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 140 | 0.5 | 570 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-006-SB2 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003914-EL-M01-006-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-006-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-007-SB2 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003914-EL-M01-007-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-007-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-008-SB2 | 1 | 0 | [32 empty] | 480 | 1.6 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003914-EL-M01-008-SB1 | 1 | 0 | [32 empty] | 480 | 1.6 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-008-SB2 | 1 | 0 | [32 empty] | 200 | 1.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-009-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-009-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-009-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-009-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-010-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003914-EL-M01-010-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-010-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-011-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003914-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-011-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-012-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-012-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-012-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003914-EL-M01-012-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-013-SB2 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003914-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003914-EL-M01-013-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid | 6003914-EL-M01-014-SB1 | 1 | 0 | [32 empty] | 1800 | 0.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC RXIL2 | 6003629-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 1800 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003629-EL-M01-007-SB2 | 1 | 0 | [32 empty] | 170 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003629-EL-M01-007-SB1 | 1 | 0 | [32 empty] | 170 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003629-EL-M01-007-SB2 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003629-EL-M01-007-SB1 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-008-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-008-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-008-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-008-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-009-SB2 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-009-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-009-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-009-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003629-EL-M01-011-SB2 | 1 | 0 | [32 empty] | 410 | 1.95 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003629-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 410 | 1.95 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ASEA Racid Af | 6003629-EL-M01-011-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Racid | 6003629-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-012-SB2 | 1 | 0 | [32 empty] | 410 | 1.95 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-012-SB1 | 1 | 0 | [32 empty] | 410 | 1.95 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-012-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-012-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-006-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-006-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-006-SB2 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-006-SB1 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-208-SB1 | 1 | 0 | [32 empty] | 410 | 1.8 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-207-SB1 | 1 | 0 | [32 empty] | 410 | 1.8 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-206-SB1 | 1 | 0 | [32 empty] | 360 | 2.3 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-205-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-204-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6004386-EL-M02-209-SB1 | 13 | 0 | [32 empty] | 300 |  | 1400 | 0.4 | 0 | 0 | 20 |  |  | 1 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Areva P122 | 6004386-EL-M02-209-SB2 | 13 | 0 | [32 empty] | 300 |  | 1400 | 0.4 | 0 | 0 | 20 |  |  | 1 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Areva P122 | 6004386-EL-M02-209-SB1 | 1 | 0 | [32 empty] | 80 | 0.4 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6004386-EL-M02-209-SB2 | 1 | 0 | [32 empty] | 80 | 0.4 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-211-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC ISM21 | 6004386-EL-M02-212-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2250 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-214-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-215-SB1 | 1 | 0 | [32 empty] | 410 | 1.8 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-216-SB1 | 1 | 0 | [32 empty] | 500 | 0.4 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC ISM21 | 6004386-EL-M02-216-SB2 | 1 | 0 | [32 empty] | 50 | 0.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M02-218-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M02-218-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M02-218-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M02-218-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-217-SB1 | 1 | 0 | [32 empty] | 410 | 2.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M02-219-SB2 | 1 | 0 | [32 empty] | 860 | 1.5 | 1900 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M02-219-SB1 | 1 | 0 | [32 empty] | 860 | 1.5 | 1900 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M02-219-SB2 | 1 | 0 | [32 empty] | 300 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M02-219-SB1 | 1 | 0 | [32 empty] | 300 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Alstom P14NB | 6004386-EL-M02-220-SB2 | 1 | 0 | [32 empty] | 450 | 1.8 | 1900 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Alstom P14NB | 6004386-EL-M02-220-SB1 | 1 | 0 | [32 empty] | 450 | 1.8 | 1900 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Alstom P14NB | 6004386-EL-M02-220-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Alstom P14NB | 6004386-EL-M02-220-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-221-SB1 | 1 | 0 | [32 empty] | 410 | 2.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-222-SB1 | 1 | 0 | [32 empty] | 420 | 2.3 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M02-223-SB1 | 1 | 0 | [32 empty] | 420 | 2.3 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-252-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-253-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-254-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-256-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-257-SB2 | 1 | 0 | [32 empty] | 720 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-257-SB1 | 1 | 0 | [32 empty] | 720 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-257-SB2 | 1 | 0 | [32 empty] | 250 | 13 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-257-SB1 | 1 | 0 | [32 empty] | 250 | 13 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-258-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-259-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-260-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-261-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-261-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-261-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M01-261-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M01-262-SB2 | 1 | 0 | [32 empty] | 860 | 1.5 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M01-262-SB1 | 1 | 0 | [32 empty] | 860 | 1.5 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M01-262-SB2 | 1 | 0 | [32 empty] | 300 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6004386-EL-M01-262-SB1 | 1 | 0 | [32 empty] | 300 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-263-SB1 | 1 | 0 | [32 empty] | 410 | 2.3 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-264-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-265-SB1 | 1 | 0 | [32 empty] | 410 | 2.3 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-266-SB1 | 1 | 0 | [32 empty] | 410 | 2.3 | 3000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC SPM | 6004386-EL-M01-268-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 3000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6008580-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 62 | 0.6 | 1240 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W3H1 | 6006114-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIM1-H | 6004348-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 250 | 1.2 | 1425 | 0.03 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6006106-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 160 | 0.5 | 630 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
BBC HB | 6003800-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIM1-H | 6003887-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1425 | 0.05 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6007733-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6007733-EL-M02-001-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6008614-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 120 | 600 | 0.5 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6007733-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6007733-EL-M02-004-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017485-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 80 | 0.5 | 360 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017485-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017369-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 300 | 0.86 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017369-EL-M02-002-SB1 | 1 | 0 | [32 empty] | 80 | 0.5 | 360 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017610-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-269-SB2 | 1 | 0 | [32 empty] | 720 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-269-SB1 | 1 | 0 | [32 empty] | 720 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-269-SB2 | 1 | 0 | [32 empty] | 250 | 13 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-269-SB1 | 1 | 0 | [32 empty] | 250 | 13 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-270-SB2 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-270-SB1 | 1 | 0 | [32 empty] | 310 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-270-SB2 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-270-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-271-SB2 | 1 | 0 | [32 empty] | 820 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-271-SB1 | 1 | 0 | [32 empty] | 820 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-271-SB2 | 1 | 0 | [32 empty] | 250 | 12 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-271-SB1 | 1 | 0 | [32 empty] | 250 | 12 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-272-SB2 | 1 | 0 | [32 empty] | 720 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-272-SB1 | 1 | 0 | [32 empty] | 720 | 2.3 | 2000 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-272-SB2 | 1 | 0 | [32 empty] | 250 | 13 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB Spaj 140C | 6004386-EL-M03-272-SB1 | 1 | 0 | [32 empty] | 250 | 13 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-007-SB1 | 1 | 0 | [32 empty] | 540 | 1.8 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-007-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6005909-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6005909-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017850-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 120 | 120 | 1500 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017850-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-012-SB1 | 1 | 0 | [32 empty] | 540 | 1.8 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-012-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-009-SB1 | 1 | 0 | [32 empty] | 540 | 1.8 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-009-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 540 | 1.8 | 1900 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 60 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6018065-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 90 | 0.5 | 360 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017828-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 720 | 1.9 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6017828-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 80 | 11 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6018093-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1000 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6018093-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6018176-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6018176-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-008-SB1 | 1 | 0 | [32 empty] | 540 | 1.9 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-008-SB1 | 1 | 0 | [32 empty] | 80 | 12 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 540 | 1.9 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-011-SB1 | 1 | 0 | [32 empty] | 80 | 12 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6018363-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 90 | 0.5 | 360 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0104243-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1120 | 0.4 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0104243-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0103157-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1100 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0103157-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 38 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0103938-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1700 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0103938-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 130 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9027619-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 75 | 0.6 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9027619-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0102951-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1120 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0102951-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-PE | 0104759-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 280 | 1.5 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-PE | 0104759-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 250 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-PE | 0104759-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 350 | 1.5 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-PE | 0104759-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 250 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0104448-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 0104448-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 250 | 0.3 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0105132-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0105132-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102449-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 0102449-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003968-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003715-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003715-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003715-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003715-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6003886-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6003880-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W1 | 9002633-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 120 | 0.6 | 720 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W1 | 9002633-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 9003207-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 9003207-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-014-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-014-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-014-SB2 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-014-SB1 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-015-SB2 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-015-SB1 | 1 | 0 | [32 empty] | 410 | 1.6 | 2000 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-015-SB2 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6003629-EL-M01-015-SB1 | 1 | 0 | [32 empty] | 80 | 9999 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1 | 6003678-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1 | 6003678-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 9003460-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 9003460-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 9003460-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 6003574-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.09 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 6003574-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003686-EL-M02-002-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003686-EL-M02-002-SB1 | 1 | 0 | [32 empty] | 40 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9026142-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1000 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9026142-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9026412-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 55 | 0.6 | 1120 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PEH | 9026412-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 9005476-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1200 | 0.05 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 6003424-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ62 | 9006373-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 150 | 0.3 | 540 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ62 | 9006373-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 150 | 0.3 | 540 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB SPAJ 140C | 9006373-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 450 | 1.2 | 1700 | 0.6 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
ABB SPAJ 140C | 9006373-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 50 | 60 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 9007176-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 9007176-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-015-SB1 | 1 | 0 | [32 empty] | 540 | 1.5 | 1600 | 0.4 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-015-SB1 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-016-SB1 | 1 | 0 | [32 empty] | 540 | 1.5 | 1600 | 0.4 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6017617-EL-M01-016-SB1 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 6006185-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 110 | 15 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 6006185-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 100 | 1.1 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4H1 | 9015643-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 140 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004334-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 30 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6004338-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6004331-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 30 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6004331-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 250 | 1.2 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004268-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 30 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
SEG WIC1-1PE | 6003809-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 120 | 0.6 | 900 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9016875-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 75 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9016875-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004265-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 20 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6004265-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 170 | 0.6 | 900 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004324-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6004321-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004321-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 150 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6004321-EL-M02-021-SB1 | 13 | 0 | [32 empty] | 55 |  | 1500 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 6004321-EL-M02-021-SB1 | 13 | 0 | [32 empty] | 40 |  | 0 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 9018722-EL-M01-011-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 9018722-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 100 | 1.2 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003427-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6003427-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 130 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003427-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 100 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003846-EL-M02-021-SB1 | 13 | 0 | [32 empty] | 20 |  | 1500 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 6003846-EL-M02-021-SB1 | 13 | 0 | [32 empty] | 20 |  | 0 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 6003846-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003846-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 120 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003846-EL-M02-024-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003846-EL-M02-024-SB1 | 1 | 0 | [32 empty] | 120 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9018724-EL-M01-011-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6003880-EL-M03-031-SB1 | 31 | 0 | [32 empty] | 30 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 9019585-EL-M01-011-SB1 | 31 | 0 | [32 empty] | 30 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6003415-EL-M03-031-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6003415-EL-M03-033-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003415-EL-M03-033-SB1 | 1 | 0 | [32 empty] | 150 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003415-EL-M03-034-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003415-EL-M03-034-SB1 | 1 | 0 | [32 empty] | 150 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003837-EL-M02-021-SB1 | 13 | 0 | [32 empty] | 55 |  | 1500 | 0 | 0 | 0 | 20 |  |  | 0.001 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 6003837-EL-M02-021-SB1 | 13 | 0 | [32 empty] | 40 |  | 0 | 0 | 0 | 0 | 20 |  |  | 0.001 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 6003837-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003837-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 120 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-003-SB2 | 1 | 0 | [32 empty] | 860 | 1.5 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 860 | 1.5 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-003-SB2 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-005-SB2 | 1 | 0 | [32 empty] | 860 | 1.5 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 860 | 1.5 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-005-SB2 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003812-EL-M02-021-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
SEG WIC1-1PE | 6006156-EL-M03-001-SB1 | 1 | 0 | [32 empty] | 54 | 0.9 | 1096 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6006156-EL-M03-005-SB1 | 1 | 0 | [32 empty] | 250 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020781-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 250 | 1.2 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020781-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 200 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020781-EL-M01-014-SB1 | 1 | 0 | [32 empty] | 170 | 1.2 | 1700 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020781-EL-M01-014-SB1 | 1 | 0 | [32 empty] | 130 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020781-EL-M01-011-SB1 | 31 | 0 | [32 empty] | 40 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
Schneider Electric P111 | 6003841-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 150 | 0.6 | 1200 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003841-EL-M02-023-SB1 | 1 | 0 | [32 empty] | 100 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003841-EL-M02-021-SB1 | 1 | 0 | [32 empty] | 35 | 0 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003841-EL-M02-021-SB1 | 1 | 0 | [32 empty] | 35 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W3 | 9021882-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W3 | 9021882-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9017588-EL-M01-011-SB1 | 31 | 0 | [32 empty] | 30 | [8 empty] | 1 | [6 empty] | 0.02 | 0.01
SEG WIC1-W3 | 9021511-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W3 | 9021511-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-PEW4 | 9021925-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 75 | 0.6 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-PEW4 | 9021925-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 60 | 0.6 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020810-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 250 | 1.2 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020810-EL-M01-013-SB1 | 1 | 0 | [32 empty] | 200 | 1.2 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020810-EL-M01-011-SB1 | 13 | 0 | [32 empty] | 20 |  | 1500 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Schneider Electric P111 | 9020810-EL-M01-011-SB1 | 13 | 0 | [32 empty] | 20 |  | 0 | 0 | 0 | 0 | 20 |  |  | 0.05 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
SEG WIC1-1PE | 0103938-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-001-SB2 | 1 | 0 | [32 empty] | 860 | 1.5 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 860 | 1.5 | 1600 | 0.3 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-001-SB2 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-001-SB1 | 1 | 0 | [32 empty] | 150 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-002-SB2 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-002-SB2 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-004-SB2 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-004-SB2 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-017-SB2 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-017-SB1 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-017-SB2 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-017-SB1 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-018-SB2 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-018-SB1 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-018-SB2 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-018-SB1 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-019-SB2 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-019-SB1 | 1 | 0 | [32 empty] | 53 | 0.1 | 75 | 0.02 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-019-SB2 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 6017617-EL-M01-019-SB1 | 1 | 0 | [32 empty] | 38 | 60 | 45 | 0.1 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020810-EL-M01-014-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 9020810-EL-M01-015-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 6003799-EL-M02-025-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6006165-EL-M02-003-SB1 | 1 | 0 | [32 empty] | 200 | 0.7 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Onbekend - | 6007734-EL-M01-002-SB1 | 1 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6018133-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 360 | 1.6 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 6018133-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 120 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 6003574-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 0.09 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-W4 | 6003574-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 60 | 10 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 0105295-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 1.5 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 0105295-EL-M01-004-SB1 | 1 | 0 | [32 empty] | 170 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 0105295-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 400 | 1.5 | 1700 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Schneider Electric P111 | 0105295-EL-M01-005-SB1 | 1 | 0 | [32 empty] | 250 | 1.5 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 0104452-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 170 | 0.9 | 1500 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Siemens 7SJ82 | 0104452-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9017226-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 150 | 0.9 | 1500 | 0.04 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
SEG WIC1-1PE | 9017226-EL-M01-003-SB1 | 1 | 0 | [32 empty] | 40 | 0.9 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6004386-EL-M02-210-SB2 | 13 | 0 | [32 empty] | 300 |  | 1400 | 0.4 | 0 | 0 | 20 |  |  | 1 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Areva P122 | 6004386-EL-M02-210-SB1 | 13 | 0 | [32 empty] | 300 |  | 1400 | 0.4 | 0 | 0 | 20 |  |  | 1 | [5 empty] | FALSE | 0.02 | 0.01 | 0.95 | 0 | 0
Areva P122 | 6004386-EL-M02-210-SB2 | 1 | 0 | [32 empty] | 80 | 0.4 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0
Areva P122 | 6004386-EL-M02-210-SB1 | 1 | 0 | [32 empty] | 80 | 0.4 | 0 | 0 | 0 | 0 | [10 empty] | 0.02 | 0.01 | 0.95 | 0

## Voltage
Name | Shortname | Unom | tinput | toutput | U< | t< | U<< | t<< | U> | t> | U>> | t>> | Ue> | te>
|  | kV | s | s | kV | s | kV | s | kV | s | kV | s | kV | s

## Distance
Name | Shortname | tinput | toutput | Ie> | I> | U< | Z< | Kn | Kn_angle | t1 | t2 | t3 | tdir | tback | tnodir
|  | s | s | A | A | kV | Ohm |  | ° | s | s | s | s | s | s
Areva PD531 | 6003914-EL-M01-002-SB1 | 0.02 | 0.01 | 200 | 200 | 0 | 0 | 2.4648 | -0.79937 | 0.03 | 0.3 | 0.9 | 2.3 | 0.6 | 0
Areva PD531 | 6003914-EL-M01-003-SB1 | 0.02 | 0.01 | 200 | 200 | 0 | 0 | 2.3904 | 0.038774 | 0.03 | 0.3 | 0.9 | 2.3 | 0.6 | 0
Areva PD531 | 6003914-EL-M01-004-SB1 | 0.02 | 0.01 | 200 | 200 | 0 | 0 | 2.4208 | -0.32827 | 0.03 | 0.3 | 0.9 | 2.3 | 0.6 | 0
Siemens 7SA82 | 6003629-EL-M01-001-SB1 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.3 | 0 | 2.3 | 0 | 0
Siemens 7SA82 | 6003629-EL-M01-002-SB1 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.3 | 0 | 2.3 | 0 | 0
Siemens 7SA82 | 6003629-EL-M01-003-SB1 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.3 | 0 | 2.3 | 0 | 0
ABB LZ91 | 6004386-EL-M02-206-SB2 | 0.02 | 0.01 | 0 | 360 | 0 | 0 | 0 | -20 | 0.03 | 0.6 | 0 | 2.3 | 0 | 0
ABB LZ91 | 6004386-EL-M02-222-SB2 | 0.02 | 0.01 | 0 | 420 | 0 | 0 | 0 | -20 | 0.03 | 0.6 | 0 | 2.3 | 0 | 0
ABB LZ91 | 6004386-EL-M02-223-SB2 | 0.02 | 0.01 | 0 | 420 | 0 | 0 | 0 | -20 | 0.03 | 0.6 | 0 | 2.3 | 0 | 0
ABB LZ91 | 6004386-EL-M01-263-SB2 | 0.02 | 0.01 | 0 | 420 | 0 | 0 | 0 | -20 | 0.03 | 0.1 | 1.9 | 2.3 | 0 | 0
ABB LZ91 | 6004386-EL-M01-265-SB2 | 0.02 | 0.01 | 0 | 420 | 0 | 0 | 0 | -20 | 0.03 | 0.1 | 1.9 | 2.3 | 0 | 0
ABB LZ91 | 6004386-EL-M01-266-SB2 | 0.02 | 0.01 | 0 | 420 | 0 | 0 | 0 | -20 | 0.03 | 0.1 | 1.9 | 2.3 | 0 | 0
AREVA P430C | 6017617-EL-M01-006-SB1 | 0.02 | 0.01 | 360 | 360 | 0 | 0 | 0.36 | -50.8 | 0.03 | 0.3 | 0 | 2.3 | 0.6 | 0
AREVA P430C | 6017617-EL-M01-014-SB1 | 0.02 | 0.01 | 360 | 360 | 0 | 0 | 0.4 | -49.9 | 0.03 | 0.3 | 0 | 2.3 | 0.6 | 0
AREVA P430C | 6017617-EL-M01-010-SB1 | 0.02 | 0.01 | 360 | 360 | 0 | 0 | 0.36 | -50.46 | 0.03 | 0.3 | 0 | 2.3 | 0.6 | 0

## Vt
Name | Ratio | Class | Capacity
VA

## Ct
Name | Ratio | Class | Capacity | Inom | Ik_dynamic | Ik_thermic | T_thermic
|  |  | VA | A | kA | kA | s

## GM
Name | Cos | Indicator | Correlation | Average[1] | Average[2] | Average[3] | Average[4] | Deviation[1] | Deviation[2] | Deviation[3] | Deviation[4] | Workday[1,1] | Workday[1,2] | Workday[1,3] | Workday[1,4] | Workday[1,5] | Workday[1,6] | Workday[1,7] | Workday[1,8] | Workday[1,9] | Workday[1,10] | Workday[1,11] | Workday[1,12] | Workday[1,13] | Workday[1,14] | Workday[1,15] | Workday[1,16] | Workday[1,17] | Workday[1,18] | Workday[1,19] | Workday[1,20] | Workday[1,21] | Workday[1,22] | Workday[1,23] | Workday[1,24] | Workday[1,25] | Workday[1,26] | Workday[1,27] | Workday[1,28] | Workday[1,29] | Workday[1,30] | Workday[1,31] | Workday[1,32] | Workday[1,33] | Workday[1,34] | Workday[1,35] | Workday[1,36] | Workday[1,37] | Workday[1,38] | Workday[1,39] | Workday[1,40] | Workday[1,41] | Workday[1,42] | Workday[1,43] | Workday[1,44] | Workday[1,45] | Workday[1,46] | Workday[1,47] | Workday[1,48] | Workday[1,49] | Workday[1,50] | Workday[1,51] | Workday[1,52] | Workday[1,53] | Workday[1,54] | Workday[1,55] | Workday[1,56] | Workday[1,57] | Workday[1,58] | Workday[1,59] | Workday[1,60] | Workday[1,61] | Workday[1,62] | Workday[1,63] | Workday[1,64] | Workday[1,65] | Workday[1,66] | Workday[1,67] | Workday[1,68] | Workday[1,69] | Workday[1,70] | Workday[1,71] | Workday[1,72] | Workday[1,73] | Workday[1,74] | Workday[1,75] | Workday[1,76] | Workday[1,77] | Workday[1,78] | Workday[1,79] | Workday[1,80] | Workday[1,81] | Workday[1,82] | Workday[1,83] | Workday[1,84] | Workday[1,85] | Workday[1,86] | Workday[1,87] | Workday[1,88] | Workday[1,89] | Workday[1,90] | Workday[1,91] | Workday[1,92] | Workday[1,93] | Workday[1,94] | Workday[1,95] | Workday[1,96] | Workday[2,1] | Workday[2,2] | Workday[2,3] | Workday[2,4] | Workday[2,5] | Workday[2,6] | Workday[2,7] | Workday[2,8] | Workday[2,9] | Workday[2,10] | Workday[2,11] | Workday[2,12] | Workday[2,13] | Workday[2,14] | Workday[2,15] | Workday[2,16] | Workday[2,17] | Workday[2,18] | Workday[2,19] | Workday[2,20] | Workday[2,21] | Workday[2,22] | Workday[2,23] | Workday[2,24] | Workday[2,25] | Workday[2,26] | Workday[2,27] | Workday[2,28] | Workday[2,29] | Workday[2,30] | Workday[2,31] | Workday[2,32] | Workday[2,33] | Workday[2,34] | Workday[2,35] | Workday[2,36] | Workday[2,37] | Workday[2,38] | Workday[2,39] | Workday[2,40] | Workday[2,41] | Workday[2,42] | Workday[2,43] | Workday[2,44] | Workday[2,45] | Workday[2,46] | Workday[2,47] | Workday[2,48] | Workday[2,49] | Workday[2,50] | Workday[2,51] | Workday[2,52] | Workday[2,53] | Workday[2,54] | Workday[2,55] | Workday[2,56] | Workday[2,57] | Workday[2,58] | Workday[2,59] | Workday[2,60] | Workday[2,61] | Workday[2,62] | Workday[2,63] | Workday[2,64] | Workday[2,65] | Workday[2,66] | Workday[2,67] | Workday[2,68] | Workday[2,69] | Workday[2,70] | Workday[2,71] | Workday[2,72] | Workday[2,73] | Workday[2,74] | Workday[2,75] | Workday[2,76] | Workday[2,77] | Workday[2,78] | Workday[2,79] | Workday[2,80] | Workday[2,81] | Workday[2,82] | Workday[2,83] | Workday[2,84] | Workday[2,85] | Workday[2,86] | Workday[2,87] | Workday[2,88] | Workday[2,89] | Workday[2,90] | Workday[2,91] | Workday[2,92] | Workday[2,93] | Workday[2,94] | Workday[2,95] | Workday[2,96] | Workday[3,1] | Workday[3,2] | Workday[3,3] | Workday[3,4] | Workday[3,5] | Workday[3,6] | Workday[3,7] | Workday[3,8] | Workday[3,9] | Workday[3,10] | Workday[3,11] | Workday[3,12] | Workday[3,13] | Workday[3,14] | Workday[3,15] | Workday[3,16] | Workday[3,17] | Workday[3,18] | Workday[3,19] | Workday[3,20] | Workday[3,21] | Workday[3,22] | Workday[3,23] | Workday[3,24] | Workday[3,25] | Workday[3,26] | Workday[3,27] | Workday[3,28] | Workday[3,29] | Workday[3,30] | Workday[3,31] | Workday[3,32] | Workday[3,33] | Workday[3,34] | Workday[3,35] | Workday[3,36] | Workday[3,37] | Workday[3,38] | Workday[3,39] | Workday[3,40] | Workday[3,41] | Workday[3,42] | Workday[3,43] | Workday[3,44] | Workday[3,45] | Workday[3,46] | Workday[3,47] | Workday[3,48] | Workday[3,49] | Workday[3,50] | Workday[3,51] | Workday[3,52] | Workday[3,53] | Workday[3,54] | Workday[3,55] | Workday[3,56] | Workday[3,57] | Workday[3,58] | Workday[3,59] | Workday[3,60] | Workday[3,61] | Workday[3,62] | Workday[3,63] | Workday[3,64] | Workday[3,65] | Workday[3,66] | Workday[3,67] | Workday[3,68] | Workday[3,69] | Workday[3,70] | Workday[3,71] | Workday[3,72] | Workday[3,73] | Workday[3,74] | Workday[3,75] | Workday[3,76] | Workday[3,77] | Workday[3,78] | Workday[3,79] | Workday[3,80] | Workday[3,81] | Workday[3,82] | Workday[3,83] | Workday[3,84] | Workday[3,85] | Workday[3,86] | Workday[3,87] | Workday[3,88] | Workday[3,89] | Workday[3,90] | Workday[3,91] | Workday[3,92] | Workday[3,93] | Workday[3,94] | Workday[3,95] | Workday[3,96] | Workday[4,1] | Workday[4,2] | Workday[4,3] | Workday[4,4] | Workday[4,5] | Workday[4,6] | Workday[4,7] | Workday[4,8] | Workday[4,9] | Workday[4,10] | Workday[4,11] | Workday[4,12] | Workday[4,13] | Workday[4,14] | Workday[4,15] | Workday[4,16] | Workday[4,17] | Workday[4,18] | Workday[4,19] | Workday[4,20] | Workday[4,21] | Workday[4,22] | Workday[4,23] | Workday[4,24] | Workday[4,25] | Workday[4,26] | Workday[4,27] | Workday[4,28] | Workday[4,29] | Workday[4,30] | Workday[4,31] | Workday[4,32] | Workday[4,33] | Workday[4,34] | Workday[4,35] | Workday[4,36] | Workday[4,37] | Workday[4,38] | Workday[4,39] | Workday[4,40] | Workday[4,41] | Workday[4,42] | Workday[4,43] | Workday[4,44] | Workday[4,45] | Workday[4,46] | Workday[4,47] | Workday[4,48] | Workday[4,49] | Workday[4,50] | Workday[4,51] | Workday[4,52] | Workday[4,53] | Workday[4,54] | Workday[4,55] | Workday[4,56] | Workday[4,57] | Workday[4,58] | Workday[4,59] | Workday[4,60] | Workday[4,61] | Workday[4,62] | Workday[4,63] | Workday[4,64] | Workday[4,65] | Workday[4,66] | Workday[4,67] | Workday[4,68] | Workday[4,69] | Workday[4,70] | Workday[4,71] | Workday[4,72] | Workday[4,73] | Workday[4,74] | Workday[4,75] | Workday[4,76] | Workday[4,77] | Workday[4,78] | Workday[4,79] | Workday[4,80] | Workday[4,81] | Workday[4,82] | Workday[4,83] | Workday[4,84] | Workday[4,85] | Workday[4,86] | Workday[4,87] | Workday[4,88] | Workday[4,89] | Workday[4,90] | Workday[4,91] | Workday[4,92] | Workday[4,93] | Workday[4,94] | Workday[4,95] | Workday[4,96] | Weekend[1,1] | Weekend[1,2] | Weekend[1,3] | Weekend[1,4] | Weekend[1,5] | Weekend[1,6] | Weekend[1,7] | Weekend[1,8] | Weekend[1,9] | Weekend[1,10] | Weekend[1,11] | Weekend[1,12] | Weekend[1,13] | Weekend[1,14] | Weekend[1,15] | Weekend[1,16] | Weekend[1,17] | Weekend[1,18] | Weekend[1,19] | Weekend[1,20] | Weekend[1,21] | Weekend[1,22] | Weekend[1,23] | Weekend[1,24] | Weekend[1,25] | Weekend[1,26] | Weekend[1,27] | Weekend[1,28] | Weekend[1,29] | Weekend[1,30] | Weekend[1,31] | Weekend[1,32] | Weekend[1,33] | Weekend[1,34] | Weekend[1,35] | Weekend[1,36] | Weekend[1,37] | Weekend[1,38] | Weekend[1,39] | Weekend[1,40] | Weekend[1,41] | Weekend[1,42] | Weekend[1,43] | Weekend[1,44] | Weekend[1,45] | Weekend[1,46] | Weekend[1,47] | Weekend[1,48] | Weekend[1,49] | Weekend[1,50] | Weekend[1,51] | Weekend[1,52] | Weekend[1,53] | Weekend[1,54] | Weekend[1,55] | Weekend[1,56] | Weekend[1,57] | Weekend[1,58] | Weekend[1,59] | Weekend[1,60] | Weekend[1,61] | Weekend[1,62] | Weekend[1,63] | Weekend[1,64] | Weekend[1,65] | Weekend[1,66] | Weekend[1,67] | Weekend[1,68] | Weekend[1,69] | Weekend[1,70] | Weekend[1,71] | Weekend[1,72] | Weekend[1,73] | Weekend[1,74] | Weekend[1,75] | Weekend[1,76] | Weekend[1,77] | Weekend[1,78] | Weekend[1,79] | Weekend[1,80] | Weekend[1,81] | Weekend[1,82] | Weekend[1,83] | Weekend[1,84] | Weekend[1,85] | Weekend[1,86] | Weekend[1,87] | Weekend[1,88] | Weekend[1,89] | Weekend[1,90] | Weekend[1,91] | Weekend[1,92] | Weekend[1,93] | Weekend[1,94] | Weekend[1,95] | Weekend[1,96] | Weekend[2,1] | Weekend[2,2] | Weekend[2,3] | Weekend[2,4] | Weekend[2,5] | Weekend[2,6] | Weekend[2,7] | Weekend[2,8] | Weekend[2,9] | Weekend[2,10] | Weekend[2,11] | Weekend[2,12] | Weekend[2,13] | Weekend[2,14] | Weekend[2,15] | Weekend[2,16] | Weekend[2,17] | Weekend[2,18] | Weekend[2,19] | Weekend[2,20] | Weekend[2,21] | Weekend[2,22] | Weekend[2,23] | Weekend[2,24] | Weekend[2,25] | Weekend[2,26] | Weekend[2,27] | Weekend[2,28] | Weekend[2,29] | Weekend[2,30] | Weekend[2,31] | Weekend[2,32] | Weekend[2,33] | Weekend[2,34] | Weekend[2,35] | Weekend[2,36] | Weekend[2,37] | Weekend[2,38] | Weekend[2,39] | Weekend[2,40] | Weekend[2,41] | Weekend[2,42] | Weekend[2,43] | Weekend[2,44] | Weekend[2,45] | Weekend[2,46] | Weekend[2,47] | Weekend[2,48] | Weekend[2,49] | Weekend[2,50] | Weekend[2,51] | Weekend[2,52] | Weekend[2,53] | Weekend[2,54] | Weekend[2,55] | Weekend[2,56] | Weekend[2,57] | Weekend[2,58] | Weekend[2,59] | Weekend[2,60] | Weekend[2,61] | Weekend[2,62] | Weekend[2,63] | Weekend[2,64] | Weekend[2,65] | Weekend[2,66] | Weekend[2,67] | Weekend[2,68] | Weekend[2,69] | Weekend[2,70] | Weekend[2,71] | Weekend[2,72] | Weekend[2,73] | Weekend[2,74] | Weekend[2,75] | Weekend[2,76] | Weekend[2,77] | Weekend[2,78] | Weekend[2,79] | Weekend[2,80] | Weekend[2,81] | Weekend[2,82] | Weekend[2,83] | Weekend[2,84] | Weekend[2,85] | Weekend[2,86] | Weekend[2,87] | Weekend[2,88] | Weekend[2,89] | Weekend[2,90] | Weekend[2,91] | Weekend[2,92] | Weekend[2,93] | Weekend[2,94] | Weekend[2,95] | Weekend[2,96] | Weekend[3,1] | Weekend[3,2] | Weekend[3,3] | Weekend[3,4] | Weekend[3,5] | Weekend[3,6] | Weekend[3,7] | Weekend[3,8] | Weekend[3,9] | Weekend[3,10] | Weekend[3,11] | Weekend[3,12] | Weekend[3,13] | Weekend[3,14] | Weekend[3,15] | Weekend[3,16] | Weekend[3,17] | Weekend[3,18] | Weekend[3,19] | Weekend[3,20] | Weekend[3,21] | Weekend[3,22] | Weekend[3,23] | Weekend[3,24] | Weekend[3,25] | Weekend[3,26] | Weekend[3,27] | Weekend[3,28] | Weekend[3,29] | Weekend[3,30] | Weekend[3,31] | Weekend[3,32] | Weekend[3,33] | Weekend[3,34] | Weekend[3,35] | Weekend[3,36] | Weekend[3,37] | Weekend[3,38] | Weekend[3,39] | Weekend[3,40] | Weekend[3,41] | Weekend[3,42] | Weekend[3,43] | Weekend[3,44] | Weekend[3,45] | Weekend[3,46] | Weekend[3,47] | Weekend[3,48] | Weekend[3,49] | Weekend[3,50] | Weekend[3,51] | Weekend[3,52] | Weekend[3,53] | Weekend[3,54] | Weekend[3,55] | Weekend[3,56] | Weekend[3,57] | Weekend[3,58] | Weekend[3,59] | Weekend[3,60] | Weekend[3,61] | Weekend[3,62] | Weekend[3,63] | Weekend[3,64] | Weekend[3,65] | Weekend[3,66] | Weekend[3,67] | Weekend[3,68] | Weekend[3,69] | Weekend[3,70] | Weekend[3,71] | Weekend[3,72] | Weekend[3,73] | Weekend[3,74] | Weekend[3,75] | Weekend[3,76] | Weekend[3,77] | Weekend[3,78] | Weekend[3,79] | Weekend[3,80] | Weekend[3,81] | Weekend[3,82] | Weekend[3,83] | Weekend[3,84] | Weekend[3,85] | Weekend[3,86] | Weekend[3,87] | Weekend[3,88] | Weekend[3,89] | Weekend[3,90] | Weekend[3,91] | Weekend[3,92] | Weekend[3,93] | Weekend[3,94] | Weekend[3,95] | Weekend[3,96] | Weekend[4,1] | Weekend[4,2] | Weekend[4,3] | Weekend[4,4] | Weekend[4,5] | Weekend[4,6] | Weekend[4,7] | Weekend[4,8] | Weekend[4,9] | Weekend[4,10] | Weekend[4,11] | Weekend[4,12] | Weekend[4,13] | Weekend[4,14] | Weekend[4,15] | Weekend[4,16] | Weekend[4,17] | Weekend[4,18] | Weekend[4,19] | Weekend[4,20] | Weekend[4,21] | Weekend[4,22] | Weekend[4,23] | Weekend[4,24] | Weekend[4,25] | Weekend[4,26] | Weekend[4,27] | Weekend[4,28] | Weekend[4,29] | Weekend[4,30] | Weekend[4,31] | Weekend[4,32] | Weekend[4,33] | Weekend[4,34] | Weekend[4,35] | Weekend[4,36] | Weekend[4,37] | Weekend[4,38] | Weekend[4,39] | Weekend[4,40] | Weekend[4,41] | Weekend[4,42] | Weekend[4,43] | Weekend[4,44] | Weekend[4,45] | Weekend[4,46] | Weekend[4,47] | Weekend[4,48] | Weekend[4,49] | Weekend[4,50] | Weekend[4,51] | Weekend[4,52] | Weekend[4,53] | Weekend[4,54] | Weekend[4,55] | Weekend[4,56] | Weekend[4,57] | Weekend[4,58] | Weekend[4,59] | Weekend[4,60] | Weekend[4,61] | Weekend[4,62] | Weekend[4,63] | Weekend[4,64] | Weekend[4,65] | Weekend[4,66] | Weekend[4,67] | Weekend[4,68] | Weekend[4,69] | Weekend[4,70] | Weekend[4,71] | Weekend[4,72] | Weekend[4,73] | Weekend[4,74] | Weekend[4,75] | Weekend[4,76] | Weekend[4,77] | Weekend[4,78] | Weekend[4,79] | Weekend[4,80] | Weekend[4,81] | Weekend[4,82] | Weekend[4,83] | Weekend[4,84] | Weekend[4,85] | Weekend[4,86] | Weekend[4,87] | Weekend[4,88] | Weekend[4,89] | Weekend[4,90] | Weekend[4,91] | Weekend[4,92] | Weekend[4,93] | Weekend[4,94] | Weekend[4,95] | Weekend[4,96] | Month[1,1] | Month[1,2] | Month[1,3] | Month[1,4] | Month[1,5] | Month[1,6] | Month[1,7] | Month[1,8] | Month[1,9] | Month[1,10] | Month[1,11] | Month[1,12] | Month[2,1] | Month[2,2] | Month[2,3] | Month[2,4] | Month[2,5] | Month[2,6] | Month[2,7] | Month[2,8] | Month[2,9] | Month[2,10] | Month[2,11] | Month[2,12] | Month[3,1] | Month[3,2] | Month[3,3] | Month[3,4] | Month[3,5] | Month[3,6] | Month[3,7] | Month[3,8] | Month[3,9] | Month[3,10] | Month[3,11] | Month[3,12] | Month[4,1] | Month[4,2] | Month[4,3] | Month[4,4] | Month[4,5] | Month[4,6] | Month[4,7] | Month[4,8] | Month[4,9] | Month[4,10] | Month[4,11] | Month[4,12] | TrendWorkday[1] | TrendWorkday[2] | TrendWorkday[3] | TrendWorkday[4] | TrendWorkday[5] | TrendWorkday[6] | TrendWorkday[7] | TrendWorkday[8] | TrendWorkday[9] | TrendWorkday[10] | TrendWorkday[11] | TrendWorkday[12] | TrendWorkday[13] | TrendWorkday[14] | TrendWorkday[15] | TrendWorkday[16] | TrendWorkday[17] | TrendWorkday[18] | TrendWorkday[19] | TrendWorkday[20] | TrendWorkday[21] | TrendWorkday[22] | TrendWorkday[23] | TrendWorkday[24] | TrendWorkday[25] | TrendWorkday[26] | TrendWorkday[27] | TrendWorkday[28] | TrendWorkday[29] | TrendWorkday[30] | TrendWorkday[31] | TrendWorkday[32] | TrendWorkday[33] | TrendWorkday[34] | TrendWorkday[35] | TrendWorkday[36] | TrendWorkday[37] | TrendWorkday[38] | TrendWorkday[39] | TrendWorkday[40] | TrendWorkday[41] | TrendWorkday[42] | TrendWorkday[43] | TrendWorkday[44] | TrendWorkday[45] | TrendWorkday[46] | TrendWorkday[47] | TrendWorkday[48] | TrendWorkday[49] | TrendWorkday[50] | TrendWorkday[51] | TrendWorkday[52] | TrendWorkday[53] | TrendWorkday[54] | TrendWorkday[55] | TrendWorkday[56] | TrendWorkday[57] | TrendWorkday[58] | TrendWorkday[59] | TrendWorkday[60] | TrendWorkday[61] | TrendWorkday[62] | TrendWorkday[63] | TrendWorkday[64] | TrendWorkday[65] | TrendWorkday[66] | TrendWorkday[67] | TrendWorkday[68] | TrendWorkday[69] | TrendWorkday[70] | TrendWorkday[71] | TrendWorkday[72] | TrendWorkday[73] | TrendWorkday[74] | TrendWorkday[75] | TrendWorkday[76] | TrendWorkday[77] | TrendWorkday[78] | TrendWorkday[79] | TrendWorkday[80] | TrendWorkday[81] | TrendWorkday[82] | TrendWorkday[83] | TrendWorkday[84] | TrendWorkday[85] | TrendWorkday[86] | TrendWorkday[87] | TrendWorkday[88] | TrendWorkday[89] | TrendWorkday[90] | TrendWorkday[91] | TrendWorkday[92] | TrendWorkday[93] | TrendWorkday[94] | TrendWorkday[95] | TrendWorkday[96] | TrendWeekend[1] | TrendWeekend[2] | TrendWeekend[3] | TrendWeekend[4] | TrendWeekend[5] | TrendWeekend[6] | TrendWeekend[7] | TrendWeekend[8] | TrendWeekend[9] | TrendWeekend[10] | TrendWeekend[11] | TrendWeekend[12] | TrendWeekend[13] | TrendWeekend[14] | TrendWeekend[15] | TrendWeekend[16] | TrendWeekend[17] | TrendWeekend[18] | TrendWeekend[19] | TrendWeekend[20] | TrendWeekend[21] | TrendWeekend[22] | TrendWeekend[23] | TrendWeekend[24] | TrendWeekend[25] | TrendWeekend[26] | TrendWeekend[27] | TrendWeekend[28] | TrendWeekend[29] | TrendWeekend[30] | TrendWeekend[31] | TrendWeekend[32] | TrendWeekend[33] | TrendWeekend[34] | TrendWeekend[35] | TrendWeekend[36] | TrendWeekend[37] | TrendWeekend[38] | TrendWeekend[39] | TrendWeekend[40] | TrendWeekend[41] | TrendWeekend[42] | TrendWeekend[43] | TrendWeekend[44] | TrendWeekend[45] | TrendWeekend[46] | TrendWeekend[47] | TrendWeekend[48] | TrendWeekend[49] | TrendWeekend[50] | TrendWeekend[51] | TrendWeekend[52] | TrendWeekend[53] | TrendWeekend[54] | TrendWeekend[55] | TrendWeekend[56] | TrendWeekend[57] | TrendWeekend[58] | TrendWeekend[59] | TrendWeekend[60] | TrendWeekend[61] | TrendWeekend[62] | TrendWeekend[63] | TrendWeekend[64] | TrendWeekend[65] | TrendWeekend[66] | TrendWeekend[67] | TrendWeekend[68] | TrendWeekend[69] | TrendWeekend[70] | TrendWeekend[71] | TrendWeekend[72] | TrendWeekend[73] | TrendWeekend[74] | TrendWeekend[75] | TrendWeekend[76] | TrendWeekend[77] | TrendWeekend[78] | TrendWeekend[79] | TrendWeekend[80] | TrendWeekend[81] | TrendWeekend[82] | TrendWeekend[83] | TrendWeekend[84] | TrendWeekend[85] | TrendWeekend[86] | TrendWeekend[87] | TrendWeekend[88] | TrendWeekend[89] | TrendWeekend[90] | TrendWeekend[91] | TrendWeekend[92] | TrendWeekend[93] | TrendWeekend[94] | TrendWeekend[95] | TrendWeekend[96] | TrendMonth[1] | TrendMonth[2] | TrendMonth[3] | TrendMonth[4] | TrendMonth[5] | TrendMonth[6] | TrendMonth[7] | TrendMonth[8] | TrendMonth[9] | TrendMonth[10] | TrendMonth[11] | TrendMonth[12]
|  |  |  | % or kW | % or kW | % or kW | % or kW | % or kW | % or kW | % or kW | % or kW

## PL
Name | Unom | Inom | Cosnom
| kV | A

## Profile
Name | Sort

## Harmonic
Name | I2 | I3 | I4 | I5 | I6 | I7 | I8 | I9 | I10 | I11 | I12 | I13 | I14 | I15 | I16 | I17 | I18 | I19 | I20 | I21 | I22 | I23 | I24 | I25 | I26 | I27 | I28 | I29 | I30 | I31 | I32 | I33 | I34 | I35 | I36 | I37 | I38 | I39 | I40 | I41 | I42 | I43 | I44 | I45 | I46 | I47 | I48 | I49 | I50 | I51 | I52 | I53 | I54 | I55 | I56 | I57 | I58 | I59 | I60 | I61 | I62 | I63 | I64 | I65 | I66 | I67 | I68 | I69 | I70 | I71 | I72 | I73 | I74 | I75 | I76 | I77 | I78 | I79 | I80 | I81 | I82 | I83 | I84 | I85 | I86 | I87 | I88 | I89 | I90 | I91 | I92 | I93 | I94 | I95 | I96 | I97 | I98 | I99 | I100 | Angle2 | Angle3 | Angle4 | Angle5 | Angle6 | Angle7 | Angle8 | Angle9 | Angle10 | Angle11 | Angle12 | Angle13 | Angle14 | Angle15 | Angle16 | Angle17 | Angle18 | Angle19 | Angle20 | Angle21 | Angle22 | Angle23 | Angle24 | Angle25 | Angle26 | Angle27 | Angle28 | Angle29 | Angle30 | Angle31 | Angle32 | Angle33 | Angle34 | Angle35 | Angle36 | Angle37 | Angle38 | Angle39 | Angle40 | Angle41 | Angle42 | Angle43 | Angle44 | Angle45 | Angle46 | Angle47 | Angle48 | Angle49 | Angle50 | Angle51 | Angle52 | Angle53 | Angle54 | Angle55 | Angle56 | Angle57 | Angle58 | Angle59 | Angle60 | Angle61 | Angle62 | Angle63 | Angle64 | Angle65 | Angle66 | Angle67 | Angle68 | Angle69 | Angle70 | Angle71 | Angle72 | Angle73 | Angle74 | Angle75 | Angle76 | Angle77 | Angle78 | Angle79 | Angle80 | Angle81 | Angle82 | Angle83 | Angle84 | Angle85 | Angle86 | Angle87 | Angle88 | Angle89 | Angle90 | Angle91 | Angle92 | Angle93 | Angle94 | Angle95 | Angle96 | Angle97 | Angle98 | Angle99 | Angle100
| % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | °

## Cable alias
Alias | Name

## Trafo alias
Alias | Name

## Coil alias
Alias | Name

## Rail alias
Alias | Name

## Fuse alias
Alias | Name

## Cabletypes
Name | Number of conductors | Shape | Type | Material | Isolation material | Conductor/isolation screen | Sheath material | Sheath/cable type | Bedding material | Arm material | Arm configuration | Arm type | Lay of wire tapes | Cable serving material | Oil duct | Pipe material | U_0 | A_cond | d_cond | d_int_cond | d_cond_ma | d_cond_mi | My_Rdc | My_ks | My_kp | t1 | delta_1 | A_she | D_she_ext | D_oc | D_ot | d_she_ma | d_she_mi | t_she | t_2 | D_arm_int | D_arm_ext | d_arm_ma | d_arm_mi | d_wire | A_tape | n_wireOrTape | D_pipe_int | D_pipe_ext | D_ext | Doga | Wiretype